## WF_Simplify
Serial Number | address in decimal | address | variable name | Permissions | meaning | Variable type | unit | usage | Low limit | High limit
1 | 64 | 0040 |  | RO | Software version (major & minor) | uint16 |  | High 8-bit major version, low 8-bit minor version
2 | 65 | 0041 |  | RO | BMS connection status | uint16 |  | 0: ID search in progress; 1: ID locked - CAN; 2: ID locked - serial port; 3: ID remotely locked.
3 | 66 | 0042 |  | RO | State machine states | uint16
4 | 67 | 0043 |  | RO | Energy terminal status | uint16
5 | 68 | 0044 |  | RO | Energy flow state | uint16
6 | 69 | 0045 |  | RO | Parallel operation | uint16
7 | 70 | 0046 |  | RO | Fault Code 1 | uint16 |  | BIT00: Mains soft start failure BIT01: Bus overvoltage BIT02: Bus undervoltage BIT03: Battery overcurrent BIT04: Overtemperature BIT05: Battery overvoltage BIT06: Battery soft start failure BIT07: Bus short circuit BIT08: Inverter soft start failure BIT09: Inverter overvoltage BIT10: Inverter undervoltage BIT11: Inverter short circuit BIT12: Negative power protection BIT13: Overload failure BIT14: Unit model and hardware incompatibility BIT15: No bootloader
8 | 71 | 0047 |  | RO | Fault Code 2 | uint16 |  | BIT00: Programming in progress BIT01: Photovoltaic reverse connection BIT02: Parallel serial number abnormal BIT03: Parallel communication abnormal BIT04: Excessive voltage difference between parallel batteries BIT05: Excessive voltage difference between parallel mains BIT06: Excessive frequency difference between parallel mains BIT07: Phase loss in parallel setting BIT08: Loss of parallel output synchronization BIT09: BMS fault BIT10: MCU fault BIT11: Reserved BIT12: Inverter load abnormal
9 | 72 | 0048 |  | RO | Alarm code 1 | uint16 |  | BIT00: Battery not connected BIT01: Battery undervoltage BIT02: Battery low voltage BIT03: Charger short circuit BIT04: Reserved BIT05: Battery overcharge BIT06: BMS lost BIT07: Overtemperature BIT08: Fan stalled BIT09: EEPROM fault BIT10: Overload BIT11: Generator waveform abnormal BIT12: Weak PV energy BIT13: Parallel synchronization signal lost BIT14: Parallel setting phase loss BIT15: Parallel version incompatible
10 | 73 | 0049 |  | RO | Alarm code 2 | uint16 |  | BIT00: Parallel communication error BIT01: Excessive voltage difference or frequency in parallel operation BIT02: Low SOC shutdown BIT03: Low SOC alarm BIT04: Excessive battery voltage difference or not connected in parallel operation BIT05: Battery short circuit BIT06: Battery voltage below starting voltage BIT07: Generator overload BIT08: Generator undervoltage BIT09: Generator overvoltage BIT10: CT reverse connection BIT11: Unstable mains power
17 | 80 | 0050 |  | RO | Phase A mains voltage | int16 | 0.1V
18 | 81 | 0051 |  | RO | Phase A mains current | int16 | 0.01A
19 | 82 | 0052 |  | RO | Phase A mains frequency | int16 | 0.01Hz
20 | 83 | 0053 |  | RO | Phase A mains power | int16 | 1W
21 | 84 | 0054 |  | RO | Phase A generator voltage | int16 | 0.1V
22 | 85 | 0055 |  | RO | Phase A generator current | int16 | 0.01A
23 | 86 | 0056 |  | RO | Phase A generator frequency | int16 | 0.01Hz
24 | 87 | 0057 |  | RO | A-phase generator power | int16 | 1W
25 | 88 | 0058 |  | RO | Phase A load voltage | int16 | 0.1V
26 | 89 | 0059 |  | RO | Phase A load current | int16 | 0.01A
27 | 90 | 005A |  | RO | Phase A load frequency | int16 | 0.01Hz
28 | 91 | 005B |  | RO | Phase A load active power | int16 | 1W
29 | 92 | 005C |  | RO | Apparent power of phase A load | int16 | 1W
30 | 93 | 005D |  | RO | Phase A load percentage | int16 | 0.1%
33 | 96 | 0060 |  | RO | Phase B mains voltage | int16 | 0.1V
34 | 97 | 0061 |  | RO | Phase B mains current | int16 | 0.01A
35 | 98 | 0062 |  | RO | Phase B mains frequency | int16 | 0.01Hz
36 | 99 | 0063 |  | RO | Phase B AC power | int16 | 1W
37 | 100 | 0064 |  | RO | B-phase generator voltage | int16 | 0.1V
38 | 101 | 0065 |  | RO | B-phase generator current | int16 | 0.01A
39 | 102 | 0066 |  | RO | B-phase generator frequency | int16 | 0.01Hz
40 | 103 | 0067 |  | RO | B-phase generator power | int16 | 1W
41 | 104 | 0068 |  | RO | Phase B load voltage | int16 | 0.1V
42 | 105 | 0069 |  | RO | B-phase load current | int16 | 0.01A
43 | 106 | 006A |  | RO | Phase B load frequency | int16 | 0.01Hz
44 | 107 | 006B |  | RO | B-phase load active power | int16 | 1W
45 | 108 | 006C |  | RO | Apparent power of phase B load | int16 | 1W
46 | 109 | 006D |  | RO | Phase B load percentage | int16 | 0.1%
49 | 112 | 0070 |  | RO | C-phase mains voltage | int16 | 0.1V
50 | 113 | 0071 |  | RO | C-phase mains current | int16 | 0.01A
51 | 114 | 0072 |  | RO | C-phase mains frequency | int16 | 0.01Hz
52 | 115 | 0073 |  | RO | C-phase mains power | int16 | 1W
53 | 116 | 0074 |  | RO | C-phase generator voltage | int16 | 0.1V
54 | 117 | 0075 |  | RO | C-phase generator current | int16 | 0.01A
55 | 118 | 0076 |  | RO | C-phase generator frequency | int16 | 0.01Hz
56 | 119 | 0077 |  | RO | C-phase generator power | int16 | 1W
57 | 120 | 0078 |  | RO | C-phase load voltage | int16 | 0.1V
58 | 121 | 0079 |  | RO | C-phase load current | int16 | 0.01A
59 | 122 | 007A |  | RO | C-phase load frequency | int16 | 0.01Hz
60 | 123 | 007B |  | RO | C-phase load active power | int16 | 1W
61 | 124 | 007C |  | RO | Apparent power of C-phase load | int16 | 1W
62 | 125 | 007D |  | RO | C-phase load percentage | int16 | 0.1%
65 | 128 | 0080 |  | RO | Positive terminal battery voltage | int16 | 0.1V
66 | 129 | 0081 |  | RO | Positive terminal battery current | int16 | 0.1A
67 | 130 | 0082 |  | RO | Negative battery voltage | int16 | 0.1V
68 | 131 | 0083 |  | RO | Negative battery current | int16 | 0.1A
69 | 132 | 0084 |  | RO | Battery capacity percentage | int16 | 0.1%
70 | 133 | 0085 |  | RO | Battery power | int16 | 1W
73 | 136 | 0088 |  | RO | BMS Battery Voltage | int16 | 0.1V
74 | 137 | 0089 |  | RO | BMS Battery Current | int16 | 0.1A
75 | 138 | 008A |  | RO | BMS SOC | int16 | %
76 | 139 | 008B |  | RO | BMS Temperature | int16 | ℃
77 | 140 | 008C |  | RO | BMS constant pressure point (CV point) | uint16 | 0.1V
78 | 141 | 008D |  | RO | Rated capacity | uint16 | 100mAH
79 | 142 | 008E |  | RO | Current capacity | uint16 | 100mAH
80 | 143 | 008F |  | RO | BMS communication status | uint16
81 | 144 | 0090 |  | RO | Lithium battery network status | uint16
82 | 145 | 0091 |  | RO | BMS failure | uint16
83 | 146 | 0092 |  | RO | BMS Alarms | uint16
87 | 150 | 0096 |  | RO | Photovoltaic voltage 1 | int16 | 0.1V
88 | 151 | 0097 |  | RO | Photovoltaic 1 current | int16 | 0.01A
89 | 152 | 0098 |  | RO | Photovoltaic power | int16 | 1W
90 | 153 | 0099 |  | RO | Photovoltaic 2 voltage | int16 | 0.1V
91 | 154 | 009A |  | RO | Photovoltaic 2 Current | int16 | 0.01A
92 | 155 | 009B |  | RO | Photovoltaic 2 power | int16 | 1W
93 | 156 | 009C |  | RO | Photovoltaic power generation on that day | uint16 | 100Wh
94 | 157 | 009D |  | RO | Total photovoltaic power generation | uint16 | 100Wh

## WF_WorkMode
Serial Number | address in decimal | address | variable name | Permissions | meaning | Variable type | unit | usage | Low limit | High limit
1 | 320 | 0140 |  | RO | Output mode | uint16 |  | 0: APP Mode; 1: UPS Mode; 2: GEN Mode (supported by some models)
2 | 321 | 0141 |  | RO | Parallel mode | uint16 |  | 0: Single-phase mode; 1: Single-phase parallel operation; 2: Three-phase parallel operation (phase A); 3: Three-phase parallel operation (phase B); 4: Three-phase parallel operation (phase C).
3 | 322 | 0142 |  | RO | Output priority | uint16 |  | 0: GBP 1: PGB 2: PBG 3: MKP (Supported by some models)
4 | 323 | 0143 |  | RO | Charging priority | uint16 |  | 0: PNG 1: OPV 2: PVF (Supported by some models)
5 | 324 | 0144 |  | RO | State machine states | uint16 |  | 0: Power On 1: Initialization 2: Standby Mode 3: AC Power Mode 4: Solar Power Mode 5: Battery Mode 6: Generator Mode 7: Fault Mode 8: Power Off Mode 9: Factory Mode 10: Upgrade Mode

## WF_BAT
Serial Number | address in decimal | address | variable name | Permissions | meaning | Variable type | unit | usage | Low limit | High limit
1 | 336 | 0150 |  | RO | Battery Type | uint16 |  | 0: Lead-acid battery; 1: Water-filled battery; 2: Ternary lithium battery; 3: Lithium iron phosphate battery; 4: Custom battery.
3 | 338 | 0152 |  | RO | Battery percentage | int16 | 1%
5 | 340 | 0154 |  | RO | Positive bus voltage | int16 | 0.1V
6 | 341 | 0155 |  | RO | Positive terminal battery voltage | int16 | 0.1V
7 | 342 | 0156 |  | RO | Negative battery discharge current | int16 | 0.1A
8 | 343 | 0157 |  | RO | Positive terminal battery charging current | int16 | 0.1A
9 | 344 | 0158 |  | RO | Positive overvoltage alarm voltage | int16 | 0.1V
10 | 345 | 0159 |  | RO | Positive terminal low voltage alarm voltage | int16 | 0.1V
13 | 348 | 015C |  | RO | Positive terminal dual-channel output cutoff voltage | int16 | 0.1V
14 | 349 | 015D |  | RO | Positive dual-channel output cutoff time | uint16 | 1H
15 | 350 | 015E |  | RO | Positive battery power | uint16 | 10W
21 | 356 | 0164 |  | RO | Negative bus voltage | int16 | 0.1V
22 | 357 | 0165 |  | RO | Negative battery voltage | int16 | 0.1V
23 | 358 | 0166 |  | RO | Negative battery discharge current | int16 | 0.1A
24 | 359 | 0167 |  | RO | Negative battery charging current | int16 | 0.1A
25 | 360 | 0168 |  | RO | Overvoltage alarm voltage at negative terminal | int16 | 0.1V
26 | 361 | 0169 |  | RO | Negative terminal low voltage alarm voltage | int16 | 0.1V
29 | 364 | 016C |  | RO | Negative terminal dual-channel output cutoff voltage | int16 | 0.1V
30 | 365 | 016D |  | RO | Negative-end dual-channel output cutoff time | uint16 | 1H
31 | 366 | 016E |  | RO | Negative battery power | uint16 | 10W
39 | 374 | 0176 |  | RO | Charging status | uint16 |  | 0: No charging; 1: Constant voltage and constant current charging; 2: Float charging; 3: Balanced charging.
40 | 375 | 0177 |  | RO | Constant voltage charging | int16 | 0.1V
41 | 376 | 0178 |  | RO | Float charging voltage | int16 | 0.1V
42 | 377 | 0179 |  | RO | Constant voltage charging current | int16 | 0.1A
43 | 378 | 017A |  | RO | float charging current | int16 | 0.1A
44 | 379 | 017B |  | RO | Longest constant current charging time | uint16 | 1H
45 | 380 | 017C |  | RO | Longest constant voltage charging time | uint16 | 1H
47 | 382 | 017E |  | RO | Equalizing charging voltage | int16 | 0.1V
48 | 383 | 017F |  | RO | Equalization charging time | uint16 | 1H
49 | 384 | 0180 |  | RO | Equalization charging delay time | uint16 | 1H
50 | 385 | 0181 |  | RO | Equalizing charging interval time | uint16 | 1D
52 | 387 | 0183 |  | RO | Equalization Interval Time Counter | uint16 | 1H

## WF_BMS
Serial Number | address in decimal | address | variable name | Permissions | meaning | Variable type | unit | usage | Low limit | High limit
1 | 400 | 0190 |  | RO | Communication Protocol | uint16 |  | reserve
2 | 401 | 0191 |  | RO | Communication status | uint16 |  | 0: ID search in progress 1: ID remote lock 2: ID lock
3 | 402 | 0192 |  | RO | Package ID | uint16
4 | 403 | 0193 |  | RO | Voltage | int16 | 0.1V
5 | 404 | 0194 |  | RO | Current | int16 | 0.1A
6 | 405 | 0195 |  | RO | temperature | int16 | 1℃
7 | 406 | 0196 |  | RO | SOC | int16 | %
8 | 407 | 0197 |  | RO | SOH | int16 | %
9 | 408 | 0198 |  | RO | Current capacity | uint16 | 10mAH
10 | 409 | 0199 |  | RO | Full charge capacity | uint16 | 10mAH
11 | 410 | 019A |  | RO | CV points | int16 | 0.1V
12 | 411 | 019B |  | RO | Maximum charging current | int16 | 0.01A
13 | 412 | 019C |  | RO | Maximum discharge current | int16 | 0.01A
14 | 413 | 019D |  | RO | Low SOC alarm points | int16 | %
15 | 414 | 019E |  | RO | Low SOC shutdown point | int16 | %
16 | 415 | 019F |  | RO | Low SOC switching point | int16 | 0.1V | reserve
17 | 416 | 01A0 |  | RO | High SOC cut battery power | int16 | 0.1V | reserve
18 | 417 | 01A1 |  | RO | Alarm | uint16
19 | 418 | 01A2 |  | RO | mistake | uint16

## WF_OP
Serial Number | address in decimal | address | variable name | Permissions | meaning | Variable type | unit | usage | Low limit | High limit
1 | 528 | 0210 |  | RO | Output priority | uint16 |  | 0:GPB 1:PGB 2:PBG 3:MKS
2 | 529 | 0211 |  | RO | Operating mode | uint16 |  | 0:APP 1:UPS 2:GEN
9 | 536 | 0218 |  | RO | A-phase output voltage | int16 | 0.1V
10 | 537 | 0219 |  | RO | Phase A output frequency | int16 | 0.01Hz
11 | 538 | 021A |  | RO | Phase A output current | int16 | 0.01A
12 | 539 | 021B |  | RO | Phase A outputs a small current. | int16 | 0.01A | reserve
13 | 540 | 021C |  | RO | Phase A output active power | int16 | 1W
14 | 541 | 021D |  | RO | Apparent power output of phase A | int16 | 1W
17 | 544 | 0220 |  | RO | Phase A load percentage | int16 | 0.1%
18 | 545 | 0221 |  | RO | A equivalent daily output power H | uint16 | 10Wh
19 | 546 | 0222 |  | RO | A equivalent daily output power L | uint16 | 10Wh
20 | 547 | 0223 |  | RO | A is equivalent to monthly output power H | uint16 | 10Wh
21 | 548 | 0224 |  | RO | A is equivalent to monthly power output L | uint16 | 10Wh
22 | 549 | 0225 |  | RO | A equivalent annual power output H | uint16 | 10Wh
23 | 550 | 0226 |  | RO | A equivalent annual power output L | uint16 | 10Wh
24 | 551 | 0227 |  | RO | Phase A total output power H | uint16 | 10Wh
25 | 552 | 0228 |  | RO | Phase A total output power L | uint16 | 10Wh
33 | 560 | 0230 |  | RO | B-phase output voltage | int16 | 0.1V
34 | 561 | 0231 |  | RO | B-phase output frequency | int16 | 0.01Hz
35 | 562 | 0232 |  | RO | B-phase output current | int16 | 0.01A
36 | 563 | 0233 |  | RO | B-phase outputs a small current. | int16 | 0.01A
37 | 564 | 0234 |  | RO | Phase B output active power | int16 | 1W
38 | 565 | 0235 |  | RO | Phase B output apparent power | int16 | 1W
41 | 568 | 0238 |  | RO | Phase B load percentage | int16 | 0.1%
42 | 569 | 0239 |  | RO | B is equivalent to daily output power H | uint16 | 10Wh
43 | 570 | 023A |  | RO | B is equivalent to daily output power L | uint16 | 10Wh
44 | 571 | 023B |  | RO | B is equivalent to monthly output power H | uint16 | 10Wh
45 | 572 | 023C |  | RO | B is equivalent to monthly output power L | uint16 | 10Wh
46 | 573 | 023D |  | RO | B is equivalent to annual power output H | uint16 | 10Wh
47 | 574 | 023E |  | RO | B is equivalent to annual power output L | uint16 | 10Wh
48 | 575 | 023F |  | RO | B-phase total output power H | uint16 | 10Wh
49 | 576 | 0240 |  | RO | Phase B total output power L | uint16 | 10Wh
57 | 584 | 0248 |  | RO | C-phase output voltage | int16 | 0.1V
58 | 585 | 0249 |  | RO | C-phase output frequency | int16 | 0.01Hz
59 | 586 | 024A |  | RO | C-phase output current | int16 | 0.01A
60 | 587 | 024B |  | RO | C-phase outputs a small current. | int16 | 0.01A
61 | 588 | 024C |  | RO | C-phase output active power | int16 | 1W
62 | 589 | 024D |  | RO | C-phase output apparent power | int16 | 1W
65 | 592 | 0250 |  | RO | C-phase load percentage | int16 | 0.1%
66 | 593 | 0251 |  | RO | C is equivalent to daily output power H | uint16 | 10Wh
67 | 594 | 0252 |  | RO | C Equivalent daily output power L | uint16 | 10Wh
68 | 595 | 0253 |  | RO | C is equivalent to monthly output power H | uint16 | 10Wh
69 | 596 | 0254 |  | RO | C is equivalent to monthly output power L | uint16 | 10Wh
70 | 597 | 0255 |  | RO | C equivalent annual power output H | uint16 | 10Wh
71 | 598 | 0256 |  | RO | C is equivalent to annual power output L | uint16 | 10Wh
72 | 599 | 0257 |  | RO | C-phase total output power H | uint16 | 10Wh
73 | 600 | 0258 |  | RO | C-phase total output power L | uint16 | 10Wh

## WF_PV
Serial Number | address in decimal | address | variable name | Permissions | meaning | Variable type | unit | usage | Low limit | High limit
1 | 608 | 0260 |  | RO | Total photovoltaic voltage | int16 | 0.1V
2 | 609 | 0261 |  | RO | Total photovoltaic current H | int16 | 0.01A
3 | 610 | 0262 |  | RO | Total photovoltaic current L | int16 | 0.01A
4 | 611 | 0263 |  | RO | Total photovoltaic power H | int16 | 1W
5 | 612 | 0264 |  | RO | Total photovoltaic power L | int16 | 1W
6 | 613 | 0265 |  | RO | Total Solar Tracking Status | int16
7 | 614 | 0266 |  | RO | Total state of solar power rechargeability | int16
8 | 615 | 0267 |  | RO | Total photovoltaic power generation H | uint16 | 10Wh
9 | 616 | 0268 |  | RO | Total photovoltaic power generation L | uint16 | 10Wh
10 | 617 | 0269 |  | RO | Total photovoltaic power generation H | uint16 | 10Wh
11 | 618 | 026A |  | RO | Total photovoltaic power generation L | uint16 | 10Wh
12 | 619 | 026B |  | RO | Total photovoltaic power generation H | uint16 | 10Wh
13 | 620 | 026C |  | RO | Total photovoltaic power generation L | uint16 | 10Wh
14 | 621 | 026D |  | RO | Total photovoltaic power generation H | uint16 | 10Wh
15 | 622 | 026E |  | RO | Total photovoltaic power generation L | uint16 | 10Wh
17 | 624 | 0270 |  | RO | Photovoltaic voltage 1 | int16 | 0.1V
18 | 625 | 0271 |  | RO | Photovoltaic 1 current | int16 | 0.01A
19 | 626 | 0272 |  | RO | Photovoltaic power | int16 | 1W
20 | 627 | 0273 |  | RO | Photovoltaic 1 tracking status | int16
21 | 628 | 0274 |  | RO | Photovoltaic 1 Rechargeable State | int16
22 | 629 | 0275 |  | RO | Photovoltaic power generation H on the day | uint16 | 10Wh
23 | 630 | 0276 |  | RO | Photovoltaic power generation L on the day | uint16 | 10Wh
24 | 631 | 0277 |  | RO | Photovoltaic power generation H in the current month | uint16 | 10Wh
25 | 632 | 0278 |  | RO | Photovoltaic power generation L in the current month | uint16 | 10Wh
26 | 633 | 0279 |  | RO | Photovoltaic power generation H in the current year | uint16 | 10Wh
27 | 634 | 027A |  | RO | Photovoltaic power generation L in the current year | uint16 | 10Wh
28 | 635 | 027B |  | RO | Total power generation H of photovoltaic 1 | uint16 | 10Wh
29 | 636 | 027C |  | RO | Photovoltaic 1 Total Power Generation L | uint16 | 10Wh
33 | 640 | 0280 |  | RO | Photovoltaic 2 voltage | int16 | 0.1V
34 | 641 | 0281 |  | RO | Photovoltaic 2 Current | int16 | 0.01A
35 | 642 | 0282 |  | RO | Photovoltaic 2 power | int16 | 1W
36 | 643 | 0283 |  | RO | Photovoltaic 2 tracking status | int16
37 | 644 | 0284 |  | RO | Photovoltaic 2 Rechargeable State | int16
38 | 645 | 0285 |  | RO | Photovoltaic 2's daily power generation H | uint16 | 10Wh
39 | 646 | 0286 |  | RO | Photovoltaic 2's daily power generation L | uint16 | 10Wh
40 | 647 | 0287 |  | RO | Photovoltaic power generation H in the current month | uint16 | 10Wh
41 | 648 | 0288 |  | RO | Photovoltaic power generation L in the current month | uint16 | 10Wh
42 | 649 | 0289 |  | RO | Photovoltaic 2's annual power generation H | uint16 | 10Wh
43 | 650 | 028A |  | RO | Photovoltaic 2's annual power generation L | uint16 | 10Wh
44 | 651 | 028B |  | RO | Photovoltaic 2 Total Power Generation H | uint16 | 10Wh
45 | 652 | 028C |  | RO | Photovoltaic 2 Total Power Generation L | uint16 | 10Wh

## WF_INV
Serial Number | address in decimal | address | variable name | Permissions | meaning | Variable type | unit | usage | Low limit | High limit
1 | 672 | 02A0 |  | RO | Inverter voltage setting value | int16 | 0.1Hz
2 | 673 | 02A1 |  | RO | Inverter frequency setting value | int16 | 0.01Hz
11 | 682 | 02AA |  | RO | A-phase inverter voltage | int16 | 0.1V
12 | 683 | 02AB |  | RO | A-phase inverter frequency | int16 | 0.01Hz
13 | 684 | 02AC |  | RO | A-phase inverter current | int16 | 0.01A
14 | 685 | 02AD |  | RO | Phase A DC component | int16 | 1mV
15 | 686 | 02AE |  | RO | Phase A Daily Input Power H | uint16 | 10W
16 | 687 | 02AF |  | RO | Phase A Daily Input Power L | uint16 | 10W
17 | 688 | 02B0 |  | RO | Phase A Monthly Input Power H | uint16 | 10W
18 | 689 | 02B1 |  | RO | Phase A Monthly Input Power L | uint16 | 10W
19 | 690 | 02B2 |  | RO | Phase A total input power H | uint16 | 10W
20 | 691 | 02B3 |  | RO | Phase A total input power L | uint16 | 10W
21 | 692 | 02B4 |  | RO | Phase A daily output power H | uint16 | 10W
22 | 693 | 02B5 |  | RO | Phase A daily output power L | uint16 | 10W
23 | 694 | 02B6 |  | RO | Phase A output power H | uint16 | 10W
24 | 695 | 02B7 |  | RO | Phase A output power L | uint16 | 10W
25 | 696 | 02B8 |  | RO | Phase A total output power H | uint16 | 10W
26 | 697 | 02B9 |  | RO | Phase A total output power L | uint16 | 10W
27 | 698 | 02BA |  | RO | B-phase inverter voltage | int16 | 0.1V
28 | 699 | 02BB |  | RO | B-phase inverter frequency | int16 | 0.01Hz
29 | 700 | 02BC |  | RO | B-phase inverter current | int16 | 0.01A
30 | 701 | 02BD |  | RO | Phase B DC component | int16 | 1mV
33 | 704 | 02C0 |  | RO | B-phase daily feeder power H | uint16 | 10W
34 | 705 | 02C1 |  | RO | B-phase daily feeder power L | uint16 | 10W
35 | 706 | 02C2 |  | RO | B-phase monthly feeder power H | uint16 | 10W
36 | 707 | 02C3 |  | RO | B-phase monthly feeder power L | uint16 | 10W
37 | 708 | 02C4 |  | RO | B-phase total grid power H | uint16 | 10W
38 | 709 | 02C5 |  | RO | B-phase total power supply L | uint16 | 10W
43 | 714 | 02CA |  | RO | C-phase inverter voltage | int16 | 0.1V
44 | 715 | 02CB |  | RO | C-phase inverter frequency | int16 | 0.01Hz
45 | 716 | 02CC |  | RO | C-phase inverter current | int16 | 0.01A
46 | 717 | 02CD |  | RO | C-phase DC component | int16 | 1mV
49 | 720 | 02D0 |  | RO | C-phase daily feeder power H | uint16 | 10W
50 | 721 | 02D1 |  | RO | C-phase daily feeder power L | uint16 | 10W
51 | 722 | 02D2 |  | RO | C-phase monthly feeder power H | uint16 | 10W
52 | 723 | 02D3 |  | RO | C-phase monthly power supply L | uint16 | 10W
53 | 724 | 02D4 |  | RO | C-phase total grid power H | uint16 | 10W
54 | 725 | 02D5 |  | RO | C-phase total grid power L | uint16 | 10W

## WF_FAN
Serial Number | address in decimal | address | variable name | Permissions | meaning | Variable type | unit | usage | Low limit | High limit
1 | 800 | 0320 |  | RO | Fan speed |  | %
2 | 801 | 0321 |  | RO | Fan status |  |  | A non-zero value indicates a stalled turn.

## WF_NTC
Serial Number | address in decimal | address | variable name | Permissions | meaning | Variable type | unit | usage | Low limit | High limit
1 | 816 | 0330 |  | RO | PV temperature |  | ℃
2 | 817 | 0331 |  | RO | INV temperature |  | ℃
3 | 818 | 0332 |  | RO | CHG temperature |  | ℃
4 | 819 | 0333 |  | RO | CHG2 temperature |  | ℃
5 | 820 | 0334 |  | RO | Ambient temperature |  | ℃
6 | 821 | 0335 |  | RO | DIS_CHG temperature |  | ℃

## WF_UserSet
Serial Number | address in decimal | address | variable name | Permissions | meaning | Variable type | unit | usage | Low limit | High limit
| 16640 | 4100 |  |  | User Settings |  |  | Note: This setting field can only be set with one parameter at a time. The host computer must ensure the accuracy of the data range set; otherwise, system malfunctions may occur. The interval between two settings should be greater than 500ms. The default display is -1/65535, indicating whether the setting was successful or not. After a successful write, a readback showing -1/65535 indicates a successful setting.
1 | 16640 | 4100 |  | RW | Output voltage | uint16 | / | 0:208V 1:220V 2:230V 3:240V
2 | 16641 | 4101 |  | RW | Output frequency | uint16 | / | 0:50Hz 1:60Hz
3 | 16642 | 4102 |  | RW | Output priority | uint16 | / | 0:GPB 1:PGB 2:PBG 3:MKS
4 | 16643 | 4103 |  | RW | Operating mode | uint16 | / | 0:APP 1:UPS
5 | 16644 | 4104 |  | RW | Charging priority | uint16 | / | 0:PNG 1:OPV 2:PVF
6 | 16645 | 4105 |  | RW | AC charging current | uint16 | 1A | 2-120A continuously adjustable [VMH6KU only supports 0x02:2A, 0x0A:10A, 0x14:20A, 0x1E:30A, 0x28:40A, 0x32:50A, 0x3C:60A, 0x46:70A, 0x50:80A, 0x5A:90A, 0x64:100A, 0x6E:110A, 0x78:120A]
7 | 16646 | 4106 |  | RW | Maximum charging current | uint16 | / | 0:2A 1:10A 2:20A 3:30A 4:40A 5:50A 6:60A 7:70A 8:80A 9:90A 10:100A 11:110A 12:120A
8 | 16647 | 4107 |  | RW | Battery Type | uint16 | / | 0: Lead-acid battery; 1: Water-filled battery; 2: Ternary lithium battery; 3: Lithium iron phosphate battery; 4: User-defined battery.
9 | 16648 | 4108 |  | RW | Battery low voltage point | uint16 | 0.1V | Lead-acid/Water-filled: 44V; Non-adjustable Ternary Lithium/Lithium Iron: 41.2V-50V; Customizable: 42V - 54V
10 | 16649 | 4109 |  | RW | Battery low voltage point (battery shutdown point) | uint16 | 0.1V | Lead-acid/Water-filled: 42V Non-adjustable ternary lithium/lithium iron phosphate/Custom: 40V-48V
11 | 16650 | 410A |  | RW | constant pressure point | uint16 | 0.1V | Lead-acid: 56.4V; Non-adjustable water-filled: 58V; Non-adjustable ternary lithium/lithium iron phosphate/custom: 48V-60V
12 | 16651 | 410B |  | RW | float point | uint16 | 0.1V | Lead-acid/Water-filled: 54V; Non-adjustable Ternary Lithium/Lithium Iron: 50V-58V; Customizable: 48V-60V
13 | 16652 | 410C |  | RW | Battery to AC voltage point | uint16 | 0.1V | Lead-acid/Water-filled: 44V - 52V; Ternary lithium/Lithium iron phosphate/Custom: 40V-50V
14 | 16653 | 410D |  | RW | Return to battery mode voltage point | uint16 | 0.1V | Lead-acid/Water-filled: 48V - 58V; Ternary lithium/Lithium iron phosphate/Custom: 46V-58V
15 | 16654 | 410E |  | RW | Low voltage point of mains power | uint16 | 1V | APP: 90V-154V UPS: 170V-200V
16 | 16655 | 410F |  | RW | High voltage point of mains power | uint16 | 1V | APP: 264V-280V UPS: 264V
17 | 16656 | 4110 |  | RW | Parallel mode | uint16 | / | 0: Single-phase mode; 1: Single-phase parallel mode; 2: Three-phase parallel mode (phase A); 3: Three-phase parallel mode (phase B); 4: Three-phase parallel mode (phase C).
18 | 16657 | 4111 |  | RW | Parallel serial number | uint16 | / | 0-14
19 | 16658 | 4112 |  | RW | Enable equalization mode for charging | uint16 | / | 0:OFF 1:ON
20 | 16659 | 4113 |  | RW | Equalization voltage point | uint16 | 0.1V | 48V-60V
21 | 16660 | 4114 |  | RW | Equalization charging time | uint16 | 1min | 5-900 step size 5
22 | 16661 | 4115 |  | RW | Equalization delay time | uint16 | 1min | 5-900 step size 5
23 | 16662 | 4116 |  | RW | Equalization interval time | uint16 | day | 1-90
24 | 16663 | 4117 |  | RW | Enable Balance Now | uint16 | / | 0:OFF 1:ON
25 | 16664 | 4118 |  | RW | Dual-channel output cutoff voltage | uint16 | 0.1V | 440-600: 44V-60V
26 | 16665 | 4119 |  | RW | Dual-channel output time | uint16 | 1min | 5-900: 5min-900min 0xFFF1: Dual output disabled 0xFFF2: Dual output unlimited time
27 | 16666 | 411A |  | RW | Generator enable | uint16 | / | 0:OFF 1:ON
28 | 16667 | 411B |  | RW | Generator rated power | uint16 | 0.1KW | 0-65:0-6.5KW
29 | 16668 | 411C |  | RW | Generator maximum power | uint16 | 0.1KW | 0-65:0-6.5KW
30 | 16669 | 411D |  | RW | Generator alarm cleared | uint16 | / | 0:OFF 1:ON
31 | 16670 | 411E |  | RW | BMS Protocol Selection | uint16 | / | 0: Disable BMS function; 1: CVTE protocol; 2: Growatt protocol; 3: Sun & Moon protocol; 4: Power protocol; 5: Tower protocol; 6: Peicheng protocol.
32 | 16671 | 411F |  | RW | BMS ID Selection | uint16 | / | 0-15 0xFFF1: ID self-search
33 | 16672 | 4120 |  | RW | Low SOC shutdown SOC settings | uint16 | 0.01 | 5-50 0xFFF1: Low SOC shutdown function for disabled users
34 | 16673 | 4121 |  | RW | Battery SOC settings | uint16 | 0.01 | 10-90 0xFFF1: Powerless SOC to Battery Function
35 | 16674 | 4122 |  | RW | SOC settings for switching to AC power | uint16 | 0.01 | 10-100 0xFFF1: Disabled SOC to AC power conversion function
36 | 16675 | 4123 |  | RW | Remote power on/off enable | uint16 | / | 0: Disable remote control; 1: Enable remote control and power on; 2: Enable remote control and power off.
37 | 16676 | 4124 |  | RW | Turn off charging | uint16 | / | 0:OFF 1:ON
38 | 16677 | 4125 |  | RW | Self-extinguishing backlight | uint16 | / | 0:OFF 1:ON
40 | 16679 | 4127 |  | RW | Overheating restart | uint16 | / | 0:OFF 1:ON
41 | 16680 | 4128 |  | RW | Overload restart | uint16 | / | 0:OFF 1:ON
42 | 16681 | 4129 |  | RW | Overload bypass | uint16 | / | 0:OFF 1:ON
43 | 16682 | 412A |  | RW | Low power consumption and energy saving | uint16 | / | 0:OFF 1:ON
44 | 16683 | 412B |  | RW | Automatic detection of mains frequency | uint16 | / | 0:OFF 1:ON
45 | 16684 | 412C |  | RW | After the output relay is closed, the inverter soft starter is activated. | uint16 | / | 0:OFF 1:ON
46 | 16685 | 412D |  | RW | Battery open circuit warning | uint16 | / | 0:OFF 1:ON
47 | 16686 | 412E |  | RW | Feeder Function Enable | uint16 | / | 0: OFF 1: INT internal sampling grid connection 2: CT external current transformer sampling grid connection 3: MET external meter communication grid connection
48 | 16687 | 412F |  | RW | Feeder power | uint16 | 0.1KW | 0-65:0-6.5KW
49 | 16688 | 4130 |  | RW | Buzzer muted | uint16 | / | 0:OFF 1:ON
50 | 16689 | 4131 |  | RW | Default return to main interface settings | uint16 | / | 0:OFF 1:ON
51 | 16690 | 4132 |  | RW | Warning of main input change | uint16 | / | 0:OFF 1:ON
52 | 16691 | 4133 |  | RW | Restore default settings | uint16 | / | 0:OFF 1:ON
53 | 16692 | 4134 |  | RW | Seconds setting | uint16 | 1 sec | 0-59
54 | 16693 | 4135 |  | RW | point | uint16 | 1min | 0-59
55 | 16694 | 4136 |  | RW | hour | uint16 | 1 hour | 0-23
56 | 16695 | 4137 |  | RW | day | uint16 | / | 0-31
57 | 16696 | 4138 |  | RW | moon | uint16 | / | 0-12
58 | 16697 | 4139 |  | RW | Year | uint16 | / | 0-99
59 | 16698 | 413A |  | RW | Power Supply 1 | uint16 | H | 0-23
60 | 16699 | 413B |  | RW | Selling electricity 1 | uint16 | H | 0-23
61 | 16700 | 413C |  | RW | Power Supply 2 | uint16 | H | 0-23
62 | 16701 | 413D |  | RW | Selling Electricity 2 | uint16 | H | 0-23
63 | 16702 | 413E |  | RW | Power on | uint16 | H | 0-23
64 | 16703 | 413F |  | RW | Power off | uint16 | H | 0-23
65 | 16704 | 4140 |  | RW | Model Configuration | uint16 |  | 0: Automatic recognition (effective after next power-on) 1: Low-end model 2: Mid-range model 3: High-end model
66 | 16705 | 4141 |  | RW | Screen type | uint16 |  | 0: TRB8131 1: B00346 2: CNKD0601/CNKD0602
67 | 16706 | 4142 |  | RW | Maximum discharge current | uint16 | A | 0-30:10-160A (step size 5A) 0xFFF1: OFF [Effective for VMH5KU/VMH6KU and VML1K2; VMH5KU supports up to 160A, VMH6KU supports up to 140A, VML1K2 supports up to 120A]
68 | 16707 | 4143 |  | RW | Wi-Fi connection status | uint16 |  | The following settings are used for the Wi-Fi module: 1: Wi-Fi not connected to a hotspot; 2: Wi-Fi connecting to a hotspot; 3: Wi-Fi already connected to a hotspot; 4: Wi-Fi already connected to a cloud server; 0xFF: Disable this flag.
69 | 16708 | 4144 |  | RW | Automatic switching of feeder power time 1 | uint16 | H | 0-23
70 | 16709 | 4145 |  | RW | Automatic switching of feeder power time 2 | uint16 | H | 0-23
71 | 16710 | 4146 |  | RW | Automatic switching of feeder power1 | uint16 | 0.1KW | 0-65:0-6.5KW
72 | 16711 | 4147 |  | RW | Automatic switching of feeder power 2 | uint16 | 0.1KW | 0-65:0-6.5KW
73 | 16712 | 4148 |  | RW | Set the fan speed to 100 before shutting down. | uint16 |  | 0: Normal operation 1: Set the fan speed to 100 before shutdown to address the issue of low-power fans not being able to shut down properly on our board [Only effective for VML1K2]
74 | 16713 | 4149 |  | RW | Set the reference value for inverter current when the output power is less than 50W. | uint16 | 0.01A | The default value is 26, and the setting range is 0-200. [Effective on VMH5KU/VMH6KU]
75 | 16714 | 414A |  | RW | Set button reverse | uint16 |  | 0: Down arrow key increments the page number; 1: Down arrow key decrements the page number. [Available in VMH5KU/VMH6KU]
76 | 16715 | 414B |  | RW | Set dual-output cutoff SOC | uint16 |  | 5-90: Dual output cutoff SOC 0xFFF1: Disable this function [Affected on VMH5KU/VMH6KU]
76 | 16715 | 414C |  | RW | Do not let the power go out | uint16 |  | 0: Invalid; 1: Disable power-off. Even if the machine is in a power-off state after setting a power-off timer, it will not enter the shutdown mode. The power-off flag is reset 1 minute after each setting, and the counter is reset each time a power-off timer is set.