## VersionInfo
Version | Author | Date | Changes
V1.0 | Huo Junhong | 2023-09-12 | Initial draft
V1.1 | Huo Junhong | 2023-11-03 | Refined the external protocol content
V1.2 | Huo Junhong | 2023-11-06 | Modified external protocol addresses, added redundancy design
V1.3 | Mao Jiankun | 2023-11-30 | Modified calibration address table, added calibration object table
V1.4 | Huo Junhong | 2023-12-10 | 1. Corrected communication format description 2. Added FCT drive enable register 3. Added address for inverter DC component register 4. Added generator-related register addresses 5. Added definition of 0x0040 field for BMS information 6. Added RTC calibration information
V1.5 | Huo Junhong | 2023-12-15 | 1. Added OTA flashing fields 2. Adjusted starting address of user parameter setting fields
V1.6 | Huo Junhong | 2024-05-22 | 1. Supplemented and organized Simplify field data 2. Removed Rated field data 3. Changed battery current unit to 0.1A 4. Added description of NTC data measurement points 5. Modified user setting method
V1.7 | Huo Junhong | 2024-06-06 | 1. Added warning code descriptions 2. Removed rated information fields 3. Removed charge mode setting field 4. Updated output priority & operating mode descriptions 5. Removed system error warning field Updated description of resettable factory settings function 6. Updated descriptions of max charge current and dual output settings 7. Added model configuration screen field
V1.8 | Huo Junhong | 2024-06-12 | 1. Added user setting current execution field 2. Changed model configuration description
V1.9 | Huo Junhong | 2024-07-03 | 1. Added description of BMS connection status 2. Corrected load percentage unit to '%' 3. Added 'GEN' to output mode, added 'MKP' to output priority, added 'PVF' to charge priority 4. Added 'Year-to-date grid feed-in total', 'Year-to-date output energy', 'Year-to-date PV generation' fields 5. Corrected FCT drive percentage unit 6. Added description of calibration object table 7. Added explanation of BMS protocol selection and ID selection 8. Added explanation of SOC-related settings 9. Removed WF_UserExecute field
V1.10 | Huo Junhong | 2024-08-11 | 1. Added Battery Power, Grid Power, and Generator Power fields (Note: these three power values are all estimates with low accuracy! Use with caution!) 2. Updated description of User Settings - Max Discharge Current field 3. Corrected units for BMS rated capacity and current capacity 4. Added usage notes for BMS-related settings
V1.11 | Huo Junhong | 2024-08-27 | 1. Added power-related data to Simplify field and adjusted data structure 2. Added consumption-only power data to Line field 3. Added explanation of some UserSet settings
V1.12 | Huo Junhong | 2024-08-27 | 1. Added setting fields related to automatic grid feed-in power switching
V1.13 | Wang Jianfei | 2024-10-29 | 1. Added factory test switch to accelerate entry into charging state (FCT) 2. Added flag to set fan speed to 100 before shutdown
V1.14 | Bai Yiting | 2024-10-30 | Added command to set the inverter current reference value when output power is below 50W
V1.15 | Mao Jiankun | 2024-11-26 | Added command to reverse button direction
V1.16 | Mao Jiankun Bai Yiting | 2025-01-08 | 1. Changed MDC setting range per VMH6KU requirements 2. Updated definition of Wifi connection flag to be compatible with different Wifi disconnect-detection requirements 3. Added PVF sub-option to charge priority 4. Added dual-output cutoff SOC function 5. Added bus voltage detection bit 6. Added button detection to FCT mode 7. Corrected fault flag definitions and descriptions 8. Defined 0x0040 as software version, with high byte = major version and low byte = minor version 9. To support WIFI interface differentiation, defined 0x0038 and 0x0039 protocol identification codes to distinguish different customers and models 10. Added definition of grid max charge current supported by certain models at 0x4105
V1.17 | Mao Jiankun | 2025-01-13 | 1. Added warnings 76 and 77: 76 = CT reverse connection, 77 = unstable grid 2. Model ID 0x0038 combines customer and model identification, 0x0039 reserved 3. Added description of the version number write flag
V1.18 | Lin Jinqiang | 2025-02-06 | 1. Added model description and parameters for 5KVMHU 2. Added definition of address 0x1020, used to read the inverter SN
V1.19 | Wang Jianfei | 2025-02-18 | 1. Added discharge temperature to NTC page
V1.20 | Mao Jiankun | 2025-02-20 | 1. Added description of the version number write flag 2. Added options for the 0x412E setting 3. Added RGB screen lock setting 0x414C

## CommFormat
Byte Count | 1 | 1 | 2 |  | 2 |  | 2
Frame Format | Slave Address | Function Code | Start Address | Start Address | Register Count High Byte | Register Count Low Byte | CRC16 | CRC16
|  |  | High Byte | Low Byte |  |  | Low Byte | High Byte
Index | Function Code | Description
1 | 0x03 | Read Data
2 | 0x10 | Write Data
Exception Code | Protocol Definition
1 | Requested function code not allowed
2 | Requested read/write address out of range
3 | Write value exceeds the upper/lower limit of the data setting
4 | No response received from communication device within 3 seconds
0x03 Standard Query Request | [8 empty] | 0x10 Standard Setting Request
Byte Count | 1 | 1 | 2 |  | 2 |  | 2 |  | Byte Count | 1 | 1 | 2 |  | 2 |  | 1 | 2N |  | 2
Frame Format | Slave Address | Function Code | Start Address |  | Register Count |  | CRC Check |  | Frame Format | Slave Address | Function Code | Start Address |  | Register Count |  | Byte Count | Data |  | CRC Check
|  |  | High Byte | Low Byte | High Byte | Low Byte | CRC Low | CRC High |  |  |  | High Byte | Low Byte | High Byte | Low Byte |  | High Byte | Low Byte | CRC Low | CRC High
Example | 01 | 03 | / | / | N |  | CRC |  | Example | 01 | 10 | / | / | N |  | 2N | / | / | CRC
0x03 Standard Query Response | [8 empty] | 0x10 Standard Setting Response
Byte Count | 1 | 1 | 1 | 2N |  | 2 |  |  | Byte Count | 1 | 1 | 2 |  | 2 |  | 2
Frame Format | Slave Address | Function Code | Byte Length | Data |  | CRC Check |  |  | Frame Format | Slave Address | Function Code | Start Address |  | Register Count |  | CRC Check
|  |  |  | High Byte | Low Byte | CRC Low | CRC High |  |  |  |  | High Byte | Low Byte | High Byte | Low Byte | CRC Low | CRC High
Example | 01 | 03 | 2N | N |  | CRC |  |  | Example | 01 | 10 | / | / | N |  | CRC
0x10 Exception Response | [8 empty] | 0x10 Exception Response
Byte Count | 1 | 1 | 1 | 2 |  |  |  |  | Byte Count | 1 | 1 | 1 | 2
Frame Format | Slave Address | Function Code | Exception Code | CRC Check |  |  |  |  | Frame Format | Slave Address | Function Code | Exception Code | CRC Check
|  |  |  | CRC Low | CRC High | [7 empty] | CRC Low | CRC High
Example | 01 | 83 | / | [5 empty] | Example | 01 | 90 | / | CRC

## WF_Version
No. | Address (Decimal) | Address | Variable Name | Permission | Meaning | Variable Type | Unit | Usage | Lower Limit | Upper Limit
| 0 | 0000 |  |  | Version Status Debug Address Set
1 | 0 | 0000 |  | Read/Write | SN Code | uint16_t
2 | 1 | 0001 |  | Read/Write | SN Code | uint16_t
3 | 2 | 0002 |  | Read/Write | SN Code | uint16_t
4 | 3 | 0003 |  | Read/Write | SN Code | uint16_t
5 | 4 | 0004 |  | Read/Write | SN Code | uint16_t
6 | 5 | 0005 |  | Read/Write | SN Code | uint16_t
7 | 6 | 0006 |  | Read/Write | SN Code | uint16_t
8 | 7 | 0007 |  | Read/Write | SN Code | uint16_t
9 | 8 | 0008 |  | Read/Write | SN Code | uint16_t
10 | 9 | 0009 |  | Read/Write | SN Code | uint16_t
11 | 10 | 000A |  | Read/Write | Reserved | uint16_t
12 | 11 | 000B |  | Read/Write | Reserved | uint16_t
13 | 12 | 000C |  | Read/Write | Reserved | uint16_t
14 | 13 | 000D |  | Read/Write | Reserved | uint16_t
15 | 14 | 000E |  | Read/Write | Reserved | uint16_t
16 | 15 | 000F |  | Read/Write | SN Code Lock | uint16_t |  | To write the SN, this register must be set to 0xA55A first; only then will the SN be saved on power loss
17 | 16 | 0010 |  | Read Only | Protocol Version_H | uint16_t
18 | 17 | 0011 |  | Read Only | Protocol Version_L | uint16_t
19 | 18 | 0012 |  | Read Only | Power Board Hardware Version_H | uint16_t
20 | 19 | 0013 |  | Read Only | Power Board Hardware Version_L | uint16_t
21 | 20 | 0014 |  | Read Only | Control Board Hardware Version_H | uint16_t
22 | 21 | 0015 |  | Read Only | Control Board Hardware Version_L | uint16_t
23 | 22 | 0016 |  | Read Only | Central Control Board Hardware Version_H | uint16_t
24 | 23 | 0017 |  | Read Only | Central Control Board Hardware Version_L | uint16_t
25 | 24 | 0018 |  | Read Only | Power Board Software Version_H | uint16_t
26 | 25 | 0019 |  | Read Only | Power Board Software Version_L | uint16_t
27 | 26 | 001A |  | Read Only | Control Board Software Version_H | uint16_t
28 | 27 | 001B |  | Read Only | Control Board Software Version_L | uint16_t
29 | 28 | 001C |  | Read Only | Central Control Board Software Version_H | uint16_t
30 | 29 | 001D |  | Read Only | Central Control Board Software Version_L | uint16_t
31 | 30 | 001E |  | Read Only | Version Date_H | uint16_t
32 | 31 | 001F |  | Read Only | Version Date_L | uint16_t
33 | 32 | 0020 |  | Read Only | CheckSum_H | uint16_t
34 | 33 | 0021 |  | Read Only | CheckSum_L | uint16_t
35 | 34 | 0022 |  | Read Only | PC Communication Protocol Version | uint16_t
36 | 35 | 0023 |  | Read Only | WiFi Communication Protocol Version | uint16_t
37 | 36 | 0024 |  | Read Only | BMS Communication Protocol Version | uint16_t
38 | 37 | 0025 |  | Read Only | Parallel Communication Protocol Version | uint16_t
39 | 38 | 0026
40 | 39 | 0027
41 | 40 | 0028
42 | 41 | 0029
43 | 42 | 002A
44 | 43 | 002B
45 | 44 | 002C
46 | 45 | 002D
47 | 46 | 002E
48 | 47 | 002F
49 | 48 | 0030
50 | 49 | 0031
51 | 50 | 0032
52 | 51 | 0033
53 | 52 | 0034
54 | 53 | 0035
55 | 54 | 0036
56 | 55 | 0037
57 | 56 | 0038 |  | Read Only | Protocol ID Code_A | uint16_t |  | Applicable customer: 0x00: Generic version 0x01: Reserved
58 | 57 | 0039 |  | Read Only | Protocol ID Code_B | uint16_t |  | Applicable model: 0x00: 6.5K 0x10: 6KU 0x20: 5KU
59 | 58 | 003A |  | Read Only | Protocol ID Code_C
60 | 59 | 003B |  | Read Only | Protocol ID Code_D
61 | 60 | 003C |  | Read Only | Device Type_H
62 | 61 | 003D |  | Read Only | Device Type_L
63 | 62 | 003E |  | Read Only | Company Info_H
64 | 63 | 003F |  | Read Only | Company Info_L

## WF_Simplify
No. | Address (Decimal) | Address | Variable Name | Permission | Meaning | Variable Type | Unit | Usage | Lower Limit | Upper Limit
| 64 | 0040 |  |  | Simplified Info Address Set
1 | 64 | 0040 |  | Read Only | Software Version (Major & Minor) | uint16_t |  | High byte = major version, low byte = minor version
2 | 65 | 0041 |  | Read Only | BMS Connection Status | uint16_t |  | 0: ID searching 1: ID locked - CAN 2: ID locked - Serial 3: ID remotely locked
3 | 66 | 0042 |  | Read Only | State Machine Status | uint16_t
4 | 67 | 0043 |  | Read Only | Energy Terminal Status | uint16_t
5 | 68 | 0044 |  | Read Only | Energy Flow Status | uint16_t
6 | 69 | 0045 |  | Read Only | Parallel Status | uint16_t
7 | 70 | 0046 |  | Read Only | Fault Code 1 | uint16_t |  | BIT00: Grid soft-start failure BIT01: Bus overvoltage BIT02: Bus undervoltage BIT03: Battery overcurrent BIT04: Over temperature BIT05: Battery overvoltage BIT06: Battery soft-start fault BIT07: Bus short circuit BIT08: Inverter soft-start fault BIT09: Inverter overvoltage BIT10: Inverter undervoltage BIT11: Inverter short circuit BIT12: Negative power protection BIT13: Overload fault BIT14: Model number does not match hardware BIT15: No bootloader
8 | 71 | 0047 |  | Read Only | Fault Code 2 | uint16_t |  | BIT00: Firmware flashing in progress BIT01: PV reverse polarity BIT02: Parallel serial number abnormal BIT03: Parallel communication abnormal BIT04: Parallel battery voltage difference too large BIT05: Parallel grid voltage difference too large BIT06: Parallel grid frequency difference too large BIT07: Parallel phase-missing setting BIT08: Parallel output sync lost BIT09: BMS fault BIT10: MCU fault BIT11: Reserved BIT12: Inverter load abnormal
9 | 72 | 0048 |  | Read Only | Warning Code 1 | uint16_t |  | BIT00: Battery not connected BIT01: Battery undervoltage BIT02: Battery low voltage BIT03: Charger short circuit BIT04: Reserved BIT05: Battery overcharge BIT06: BMS lost BIT07: Over temperature BIT08: Fan locked BIT09: EEPROM fault BIT10: Overload BIT11: Generator waveform abnormal BIT12: Weak PV energy BIT13: Parallel sync signal lost BIT14: Parallel phase-missing setting BIT15: Parallel version incompatible
10 | 73 | 0049 |  | Read Only | Warning Code 2 | uint16_t |  | BIT00: Parallel communication abnormal BIT01: Parallel grid voltage/frequency difference too large BIT02: Low SOC shutdown BIT03: Low SOC warning BIT04: Parallel battery voltage difference too large or not connected BIT05: Battery short circuit BIT06: Battery below start voltage BIT07: Generator overload BIT08: Generator undervoltage BIT09: Generator overvoltage BIT10: CT reverse connection BIT11: Grid unstable
11 | 74 | 004A
12 | 75 | 004B
13 | 76 | 004C
14 | 77 | 004D
15 | 78 | 004E
16 | 79 | 004F
17 | 80 | 0050 |  | Read Only | Phase A Grid Voltage | int16_t | 0.1V
18 | 81 | 0051 |  | Read Only | Phase A Grid Current | int16_t | 0.01A
19 | 82 | 0052 |  | Read Only | Phase A Grid Frequency | int16_t | 0.01Hz
20 | 83 | 0053 |  | Read Only | Phase A Grid Power | int16_t | 1W
21 | 84 | 0054 |  | Read Only | Phase A Generator Voltage | int16_t | 0.1V
22 | 85 | 0055 |  | Read Only | Phase A Generator Current | int16_t | 0.01A
23 | 86 | 0056 |  | Read Only | Phase A Generator Frequency | int16_t | 0.01Hz
24 | 87 | 0057 |  | Read Only | Phase A Generator Power | int16_t | 1W
25 | 88 | 0058 |  | Read Only | Phase A Load Voltage | int16_t | 0.1V
26 | 89 | 0059 |  | Read Only | Phase A Load Current | int16_t | 0.01A
27 | 90 | 005A |  | Read Only | Phase A Load Frequency | int16_t | 0.01Hz
28 | 91 | 005B |  | Read Only | Phase A Load Active Power | int16_t | 1W
29 | 92 | 005C |  | Read Only | Phase A Load Apparent Power | int16_t | 1W
30 | 93 | 005D |  | Read Only | Phase A Load Percentage | int16_t | 0.1%
31 | 94 | 005E
32 | 95 | 005F
33 | 96 | 0060 |  | Read Only | Phase B Grid Voltage | int16_t | 0.1V
34 | 97 | 0061 |  | Read Only | Phase B Grid Current | int16_t | 0.01A
35 | 98 | 0062 |  | Read Only | Phase B Grid Frequency | int16_t | 0.01Hz
36 | 99 | 0063 |  | Read Only | Phase B Grid Power | int16_t | 1W
37 | 100 | 0064 |  | Read Only | Phase B Generator Voltage | int16_t | 0.1V
38 | 101 | 0065 |  | Read Only | Phase B Generator Current | int16_t | 0.01A
39 | 102 | 0066 |  | Read Only | Phase B Generator Frequency | int16_t | 0.01Hz
40 | 103 | 0067 |  | Read Only | Phase B Generator Power | int16_t | 1W
41 | 104 | 0068 |  | Read Only | Phase B Load Voltage | int16_t | 0.1V
42 | 105 | 0069 |  | Read Only | Phase B Load Current | int16_t | 0.01A
43 | 106 | 006A |  | Read Only | Phase B Load Frequency | int16_t | 0.01Hz
44 | 107 | 006B |  | Read Only | Phase B Load Active Power | int16_t | 1W
45 | 108 | 006C |  | Read Only | Phase B Load Apparent Power | int16_t | 1W
46 | 109 | 006D |  | Read Only | Phase B Load Percentage | int16_t | 0.1%
47 | 110 | 006E
48 | 111 | 006F
49 | 112 | 0070 |  | Read Only | Phase C Grid Voltage | int16_t | 0.1V
50 | 113 | 0071 |  | Read Only | Phase C Grid Current | int16_t | 0.01A
51 | 114 | 0072 |  | Read Only | Phase C Grid Frequency | int16_t | 0.01Hz
52 | 115 | 0073 |  | Read Only | Phase C Grid Power | int16_t | 1W
53 | 116 | 0074 |  | Read Only | Phase C Generator Voltage | int16_t | 0.1V
54 | 117 | 0075 |  | Read Only | Phase C Generator Current | int16_t | 0.01A
55 | 118 | 0076 |  | Read Only | Phase C Generator Frequency | int16_t | 0.01Hz
56 | 119 | 0077 |  | Read Only | Phase C Generator Power | int16_t | 1W
57 | 120 | 0078 |  | Read Only | Phase C Load Voltage | int16_t | 0.1V
58 | 121 | 0079 |  | Read Only | Phase C Load Current | int16_t | 0.01A
59 | 122 | 007A |  | Read Only | Phase C Load Frequency | int16_t | 0.01Hz
60 | 123 | 007B |  | Read Only | Phase C Load Active Power | int16_t | 1W
61 | 124 | 007C |  | Read Only | Phase C Load Apparent Power | int16_t | 1W
62 | 125 | 007D |  | Read Only | Phase C Load Percentage | int16_t | 0.1%
63 | 126 | 007E
64 | 127 | 007F
65 | 128 | 0080 |  | Read Only | Positive Terminal Battery Voltage | int16_t | 0.1V
66 | 129 | 0081 |  | Read Only | Positive Terminal Battery Current | int16_t | 0.1A
67 | 130 | 0082 |  | Read Only | Negative Terminal Battery Voltage | int16_t | 0.1V
68 | 131 | 0083 |  | Read Only | Negative Terminal Battery Current | int16_t | 0.1A
69 | 132 | 0084 |  | Read Only | Battery Capacity Percentage | int16_t | 0.1%
70 | 133 | 0085 |  | Read Only | Battery Power | int16_t | 1W
71 | 134 | 0086
72 | 135 | 0087
73 | 136 | 0088 |  | Read Only | BMS Battery Voltage | int16_t | 0.1V
74 | 137 | 0089 |  | Read Only | BMS Battery Current | int16_t | 0.1A
75 | 138 | 008A |  | Read Only | BMS SOC | int16_t | %
76 | 139 | 008B |  | Read Only | BMS Temperature | int16_t | ℃
77 | 140 | 008C |  | Read Only | BMS Constant Voltage Point (CV Point) | uint16_t | 0.1V
78 | 141 | 008D |  | Read Only | Rated Capacity | uint16_t | 100mAH
79 | 142 | 008E |  | Read Only | Current Capacity | uint16_t | 100mAH
80 | 143 | 008F |  | Read Only | BMS Communication Status | uint16_t
81 | 144 | 0090 |  | Read Only | Lithium Battery Networking Status | uint16_t
82 | 145 | 0091 |  | Read Only | BMS Fault | uint16_t
83 | 146 | 0092 |  | Read Only | BMS Warning | uint16_t
84 | 147 | 0093
85 | 148 | 0094
86 | 149 | 0095
87 | 150 | 0096 |  | Read Only | PV1 Voltage | int16_t | 0.1V
88 | 151 | 0097 |  | Read Only | PV1 Current | int16_t | 0.01A
89 | 152 | 0098 |  | Read Only | PV1 Power | int16_t | 1W
90 | 153 | 0099 |  | Read Only | PV2 Voltage | int16_t | 0.1V
91 | 154 | 009A |  | Read Only | PV2 Current | int16_t | 0.01A
92 | 155 | 009B |  | Read Only | PV2 Power | int16_t | 1W
93 | 156 | 009C |  | Read Only | Today's PV Generation | uint16_t | 100Wh
94 | 157 | 009D |  | Read Only | Total PV Generation | uint16_t | 100Wh
95 | 158 | 009E
96 | 159 | 009F

## WF_WorkMode
No. | Address (Decimal) | Address | Variable Name | Permission | Meaning | Variable Type | Unit | Usage | Lower Limit | Upper Limit
| 320 | 0140 |  | Read Only | Working Mode
1 | 320 | 0140 |  | Read Only | Output Mode | uint16_t |  | 0: APP Mode 1: UPS Mode 2: GEN Mode (supported on some models)
2 | 321 | 0141 |  | Read Only | Parallel Mode | uint16_t |  | 0: Single-unit mode 1: Single-phase parallel 2: Three-phase parallel, Phase A 3: Three-phase parallel, Phase B 4: Three-phase parallel, Phase C
3 | 322 | 0142 |  | Read Only | Output Priority | uint16_t |  | 0: GPB 1: PGB 2: PBG 3: MKP (supported on some models)
4 | 323 | 0143 |  | Read Only | Charge Priority | uint16_t |  | 0: PNG 1: OPV 2: PVF (supported on some models)
5 | 324 | 0144 |  | Read Only | State Machine Status | uint16_t |  | 0: Power on 1: Initialization 2: Standby mode 3: Grid mode 4: PV mode 5: Battery mode 6: Generator mode 7: Fault mode 8: Shutdown mode 9: Factory mode 10: Upgrade mode
6 | 325 | 0145
7 | 326 | 0146
8 | 327 | 0147
9 | 328 | 0148
10 | 329 | 0149
11 | 330 | 014A
12 | 331 | 014B
13 | 332 | 014C
14 | 333 | 014D
15 | 334 | 014E
16 | 335 | 014F

## WF_BAT
No. | Address (Decimal) | Address | Variable Name | Permission | Meaning | Variable Type | Unit | Usage | Lower Limit | Upper Limit
| 336 | 0150 |  |  | Battery Info Address Set
1 | 336 | 0150 |  | Read Only | Battery Type | uint16_t |  | 0: Lead-acid battery 1: Flooded battery 2: Ternary lithium (NMC) battery 3: LiFePO4 battery 4: Custom battery
2 | 337 | 0151 |  | Read Only
3 | 338 | 0152 |  | Read Only | Battery Charge Percentage | int16_t | 1%
4 | 339 | 0153 |  | Read Only
5 | 340 | 0154 |  | Read Only | Positive Terminal Bus Voltage | int16_t | 0.1V
6 | 341 | 0155 |  | Read Only | Positive Terminal Battery Voltage | int16_t | 0.1V
7 | 342 | 0156 |  | Read Only | Negative Terminal Battery Discharge Current | int16_t | 0.1A
8 | 343 | 0157 |  | Read Only | Positive Terminal Battery Charge Current | int16_t | 0.1A
9 | 344 | 0158 |  | Read Only | Positive Terminal Overvoltage Warning Voltage | int16_t | 0.1V
10 | 345 | 0159 |  | Read Only | Positive Terminal Low Voltage Warning Voltage | int16_t | 0.1V
11 | 346 | 015A
12 | 347 | 015B
13 | 348 | 015C |  | Read Only | Positive Terminal Dual-Output Cutoff Voltage | int16_t | 0.1V
14 | 349 | 015D |  | Read Only | Positive Terminal Dual-Output Cutoff Time | uint16_t | 1H
15 | 350 | 015E |  | Read Only | Positive Terminal Battery Power | uint16_t | 10W
16 | 351 | 015F
17 | 352 | 0160
18 | 353 | 0161
19 | 354 | 0162
20 | 355 | 0163
21 | 356 | 0164 |  | Read Only | Negative Terminal Bus Voltage | int16_t
22 | 357 | 0165 |  | Read Only | Negative Terminal Battery Voltage | int16_t
23 | 358 | 0166 |  | Read Only | Negative Terminal Battery Discharge Current | int16_t | 0.1A
24 | 359 | 0167 |  | Read Only | Negative Terminal Battery Charge Current | int16_t | 0.1A
25 | 360 | 0168 |  | Read Only | Negative Terminal Overvoltage Warning Voltage | int16_t | 0.1V
26 | 361 | 0169 |  | Read Only | Negative Terminal Low Voltage Warning Voltage | int16_t | 0.1V
27 | 362 | 016A
28 | 363 | 016B
29 | 364 | 016C |  | Read Only | Negative Terminal Dual-Output Cutoff Voltage | int16_t | 0.1V
30 | 365 | 016D |  | Read Only | Negative Terminal Dual-Output Cutoff Time | uint16_t | 1H
31 | 366 | 016E |  | Read Only | Negative Terminal Battery Power | uint16_t | 10W
32 | 367 | 016F
33 | 368 | 0170
34 | 369 | 0171
35 | 370 | 0172
36 | 371 | 0173
37 | 372 | 0174
38 | 373 | 0175
39 | 374 | 0176 |  | Read Only | Charging Status | uint16_t |  | 0: No charging 1: Constant voltage/constant current charging 2: Float charging 3: Equalization charging
40 | 375 | 0177 |  | Read Only | Constant Voltage Charge Voltage | int16_t | 0.1V
41 | 376 | 0178 |  | Read Only | Float Charge Voltage | int16_t | 0.1V
42 | 377 | 0179 |  | Read Only | Constant Voltage Charge Current | int16_t | 0.1A
43 | 378 | 017A |  | Read Only | Float Charge Current | int16_t | 0.1A
44 | 379 | 017B |  | Read Only | Max Constant Current Charging Time | uint16_t | 1H
45 | 380 | 017C |  | Read Only | Max Constant Voltage Charging Time | uint16_t | 1H
46 | 381 | 017D
47 | 382 | 017E |  | Read Only | Equalization Charge Voltage | int16_t | 0.1V
48 | 383 | 017F |  | Read Only | Equalization Charge Time | uint16_t | 1H
49 | 384 | 0180 |  | Read Only | Equalization Charge Delay Time | uint16_t | 1H
50 | 385 | 0181 |  | Read Only | Equalization Charge Interval | uint16_t | 1D
51 | 386 | 0182
52 | 387 | 0183 |  | Read Only | Equalization Interval Counter | uint16_t | 1H
53 | 388 | 0184
54 | 389 | 0185
55 | 390 | 0186
56 | 391 | 0187
57 | 392 | 0188
58 | 393 | 0189
59 | 394 | 018A
60 | 395 | 018B
61 | 396 | 018C
62 | 397 | 018D
63 | 398 | 018E
64 | 399 | 018F

## WF_BMS
No. | Address (Decimal) | Address | Variable Name | Permission | Meaning | Variable Type | Unit | Usage | Lower Limit | Upper Limit
| 400 | 0190 |  |  | BMS Debug Address Set
1 | 400 | 0190 |  | Read Only | Communication Protocol | uint16_t |  | Reserved
2 | 401 | 0191 |  | Read Only | Communication Status | uint16_t |  | 0: ID searching 1: ID remotely locked 2: ID locked
3 | 402 | 0192 |  | Read Only | Pack ID | uint16_t
4 | 403 | 0193 |  | Read Only | Voltage | int16_t | 0.1V
5 | 404 | 0194 |  | Read Only | Current | int16_t | 0.1A
6 | 405 | 0195 |  | Read Only | Temperature | int16_t | 1℃
7 | 406 | 0196 |  | Read Only | SOC | int16_t | %
8 | 407 | 0197 |  | Read Only | SOH | int16_t | %
9 | 408 | 0198 |  | Read Only | Current Capacity | uint16_t | 10mAH
10 | 409 | 0199 |  | Read Only | Full Charge Capacity | uint16_t | 10mAH
11 | 410 | 019A |  | Read Only | CV Point | int16_t | 0.1V
12 | 411 | 019B |  | Read Only | Max Charge Current | int16_t | 0.01A
13 | 412 | 019C |  | Read Only | Max Discharge Current | int16_t | 0.01A
14 | 413 | 019D |  | Read Only | Low SOC Warning Point | int16_t | %
15 | 414 | 019E |  | Read Only | Low SOC Shutdown Point | int16_t | %
16 | 415 | 019F |  | Read Only | Low SOC Switch-to-Grid Point | int16_t | 0.1V | Reserved
17 | 416 | 01A0 |  | Read Only | High SOC Switch-to-Battery Point | int16_t | 0.1V | Reserved
18 | 417 | 01A1 |  | Read Only | Warning | uint16_t
19 | 418 | 01A2 |  | Read Only | Error | uint16_t
20 | 419 | 01A3
21 | 420 | 01A4
22 | 421 | 01A5
23 | 422 | 01A6
24 | 423 | 01A7
25 | 424 | 01A8
26 | 425 | 01A9
27 | 426 | 01AA
28 | 427 | 01AB
29 | 428 | 01AC
30 | 429 | 01AD
31 | 430 | 01AE
32 | 431 | 01AF

## WF_LINE
No. | Address (Decimal) | Address | Variable Name | Permission | Meaning | Variable Type | Unit | Usage | Lower Limit | Upper Limit
| 432 | 01B0 |  |  | Grid Status Debug Address Set
1 | 432 | 01B0 |  | Read Only | Phase A Grid Voltage | int16_t | 0.1V
2 | 433 | 01B1 |  | Read Only | Phase A Grid Current | int16_t | 0.01A
3 | 434 | 01B2 |  | Read Only | Phase A Grid Frequency | int16_t | 0.01Hz
4 | 435 | 01B3 |  | Read Only | Phase A Grid Power | int16_t | 10W
5 | 436 | 01B4 |  | Read Only | Phase A Grid Power (Consumption Only) | int16_t | 10W
6 | 437 | 01B5
7 | 438 | 01B6
8 | 439 | 01B7 |  | Read Only | Phase A Today's Grid Feed-in Total_H | uint16_t | 10Wh
9 | 440 | 01B8 |  | Read Only | Phase A Today's Grid Feed-in Total_L | uint16_t | 10Wh
10 | 441 | 01B9 |  | Read Only | Phase A This Month's Grid Feed-in Total_H | uint16_t | 10Wh
11 | 442 | 01BA |  | Read Only | Phase A This Month's Grid Feed-in Total_L | uint16_t | 10Wh
12 | 443 | 01BB |  | Read Only | Phase A This Year's Grid Feed-in Total_H | uint16_t | 10Wh
13 | 444 | 01BC |  | Read Only | Phase A This Year's Grid Feed-in Total_L | uint16_t | 10Wh
14 | 445 | 01BD |  | Read Only | Phase A Total Grid Feed-in_H | uint16_t | 10Wh
15 | 446 | 01BE |  | Read Only | Phase A Total Grid Feed-in_L | uint16_t | 10Wh
16 | 447 | 01BF |  | Read Only | Phase A Today's Grid Consumption Total_H | uint16_t | 10Wh
17 | 448 | 01C0 |  | Read Only | Phase A Today's Grid Consumption Total_L | uint16_t | 10Wh
18 | 449 | 01C1 |  | Read Only | Phase A This Month's Grid Consumption Total_H | uint16_t | 10Wh
19 | 450 | 01C2 |  | Read Only | Phase A This Month's Grid Consumption Total_L | uint16_t | 10Wh
20 | 451 | 01C3 |  | Read Only | Phase A This Year's Grid Consumption Total_H | uint16_t | 10Wh
21 | 452 | 01C4 |  | Read Only | Phase A This Year's Grid Consumption Total_L | uint16_t | 10Wh
22 | 453 | 01C5 |  | Read Only | Phase A Total Grid Consumption_H | uint16_t | 10Wh
23 | 454 | 01C6 |  | Read Only | Phase A Total Grid Consumption_L | uint16_t | 10Wh
24 | 455 | 01C7
25 | 456 | 01C8
26 | 457 | 01C9
27 | 458 | 01CA
28 | 459 | 01CB
29 | 460 | 01CC
30 | 461 | 01CD
31 | 462 | 01CE
32 | 463 | 01CF
33 | 464 | 01D0 |  | Read Only | Phase B Grid Voltage | int16_t | 0.1V
34 | 465 | 01D1 |  | Read Only | Phase B Grid Current | int16_t | 0.01A
35 | 466 | 01D2 |  | Read Only | Phase B Grid Frequency | int16_t | 0.01Hz
36 | 467 | 01D3 |  | Read Only | Phase B Grid Power | int16_t | 10W
37 | 468 | 01D4 |  | Read Only | Phase B Grid Power (Consumption Only) | int16_t | 10W
38 | 469 | 01D5
39 | 470 | 01D6
40 | 471 | 01D7 |  | Read Only | Phase B Today's Grid Feed-in Total_H | uint16_t | 10Wh
41 | 472 | 01D8 |  | Read Only | Phase B Today's Grid Feed-in Total_L | uint16_t | 10Wh
42 | 473 | 01D9 |  | Read Only | Phase B This Month's Grid Feed-in Total_H | uint16_t | 10Wh
43 | 474 | 01DA |  | Read Only | Phase B This Month's Grid Feed-in Total_L | uint16_t | 10Wh
44 | 475 | 01DB |  | Read Only | Phase B This Year's Grid Feed-in Total_H | uint16_t | 10Wh
45 | 476 | 01DC |  | Read Only | Phase B This Year's Grid Feed-in Total_L | uint16_t | 10Wh
46 | 477 | 01DD |  | Read Only | Phase B Total Grid Feed-in_H | uint16_t | 10Wh
47 | 478 | 01DE |  | Read Only | Phase B Total Grid Feed-in_L | uint16_t | 10Wh
48 | 479 | 01DF |  | Read Only | Phase B Today's Grid Consumption Total_H | uint16_t | 10Wh
49 | 480 | 01E0 |  | Read Only | Phase B Today's Grid Consumption Total_L | uint16_t | 10Wh
50 | 481 | 01E1 |  | Read Only | Phase B This Month's Grid Consumption Total_H | uint16_t | 10Wh
51 | 482 | 01E2 |  | Read Only | Phase B This Month's Grid Consumption Total_L | uint16_t | 10Wh
52 | 483 | 01E3 |  | Read Only | Phase B This Year's Grid Consumption Total_H | uint16_t | 10Wh
53 | 484 | 01E4 |  | Read Only | Phase B This Year's Grid Consumption Total_L | uint16_t | 10Wh
54 | 485 | 01E5 |  | Read Only | Phase B Total Grid Consumption_H | uint16_t | 10Wh
55 | 486 | 01E6 |  | Read Only | Phase B Total Grid Consumption_L | uint16_t | 10Wh
56 | 487 | 01E7
57 | 488 | 01E8
58 | 489 | 01E9
59 | 490 | 01EA
60 | 491 | 01EB
61 | 492 | 01EC
62 | 493 | 01ED
63 | 494 | 01EE
64 | 495 | 01EF
65 | 496 | 01F0 |  | Read Only | Phase C Grid Voltage | int16_t | 0.1V
66 | 497 | 01F1 |  | Read Only | Phase C Grid Current | int16_t | 0.01A
67 | 498 | 01F2 |  | Read Only | Phase C Grid Frequency | int16_t | 0.01Hz
68 | 499 | 01F3 |  | Read Only | Phase C Grid Power | int16_t | 10W
69 | 500 | 01F4 |  | Read Only | Phase C Grid Power (Consumption Only) | int16_t | 10W
70 | 501 | 01F5
71 | 502 | 01F6
72 | 503 | 01F7 |  | Read Only | Phase C Today's Grid Feed-in Total_H | uint16_t | 10Wh
73 | 504 | 01F8 |  | Read Only | Phase C Today's Grid Feed-in Total_L | uint16_t | 10Wh
74 | 505 | 01F9 |  | Read Only | Phase C This Month's Grid Feed-in Total_H | uint16_t | 10Wh
75 | 506 | 01FA |  | Read Only | Phase C This Month's Grid Feed-in Total_L | uint16_t | 10Wh
76 | 507 | 01FB |  | Read Only | Phase C This Year's Grid Feed-in Total_H | uint16_t | 10Wh
77 | 508 | 01FC |  | Read Only | Phase C This Year's Grid Feed-in Total_L | uint16_t | 10Wh
78 | 509 | 01FD |  | Read Only | Phase C Total Grid Feed-in_H | uint16_t | 10Wh
79 | 510 | 01FE |  | Read Only | Phase C Total Grid Feed-in_L | uint16_t | 10Wh
80 | 511 | 01FF |  | Read Only | Phase C Today's Grid Consumption Total_H | uint16_t | 10Wh
81 | 512 | 0200 |  | Read Only | Phase C Today's Grid Consumption Total_L | uint16_t | 10Wh
82 | 513 | 0201 |  | Read Only | Phase C This Month's Grid Consumption Total_H | uint16_t | 10Wh
83 | 514 | 0202 |  | Read Only | Phase C This Month's Grid Consumption Total_L | uint16_t | 10Wh
84 | 515 | 0203 |  | Read Only | Phase C This Year's Grid Consumption Total_H | uint16_t | 10Wh
85 | 516 | 0204 |  | Read Only | Phase C This Year's Grid Consumption Total_L | uint16_t | 10Wh
86 | 517 | 0205 |  | Read Only | Phase C Total Grid Consumption_H | uint16_t | 10Wh
87 | 518 | 0206 |  | Read Only | Phase C Total Grid Consumption_L | uint16_t | 10Wh
88 | 519 | 0207
89 | 520 | 0208
90 | 521 | 0209
91 | 522 | 020A
92 | 523 | 020B
93 | 524 | 020C
94 | 525 | 020D
95 | 526 | 020E
96 | 527 | 020F

## WF_OP
No. | Address (Decimal) | Address | Variable Name | Permission | Meaning | Variable Type | Unit | Usage | Lower Limit | Upper Limit
| 528 | 0210 |  |  | Output Debug Address Set
1 | 528 | 0210 |  | Read Only | Output Priority | uint16_t |  | 0:GPB 1:PGB 2:PBG 3:MKS
2 | 529 | 0211 |  | Read Only | Operating Mode | uint16_t |  | 0:APP 1:UPS 2:GEN
3 | 530 | 0212
4 | 531 | 0213
5 | 532 | 0214
6 | 533 | 0215
7 | 534 | 0216
8 | 535 | 0217
9 | 536 | 0218 |  | Read Only | Phase A Output Voltage | int16_t | 0.1V
10 | 537 | 0219 |  | Read Only | Phase A Output Frequency | int16_t | 0.01Hz
11 | 538 | 021A |  | Read Only | Phase A Output Current | int16_t | 0.01A
12 | 539 | 021B |  | Read Only | Phase A Output Low-Range Current | int16_t | 0.01A | Reserved
13 | 540 | 021C |  | Read Only | Phase A Output Active Power | int16_t | 1W
14 | 541 | 021D |  | Read Only | Phase A Output Apparent Power | int16_t | 1W
15 | 542 | 021E
16 | 543 | 021F
17 | 544 | 0220 |  | Read Only | Phase A Load Percentage | int16_t | 0.1%
18 | 545 | 0221 |  | Read Only | Phase A Today's Output Energy_H | uint16_t | 10Wh
19 | 546 | 0222 |  | Read Only | Phase A Today's Output Energy_L | uint16_t | 10Wh
20 | 547 | 0223 |  | Read Only | Phase A This Month's Output Energy_H | uint16_t | 10Wh
21 | 548 | 0224 |  | Read Only | Phase A This Month's Output Energy_L | uint16_t | 10Wh
22 | 549 | 0225 |  | Read Only | Phase A This Year's Output Energy_H | uint16_t | 10Wh
23 | 550 | 0226 |  | Read Only | Phase A This Year's Output Energy_L | uint16_t | 10Wh
24 | 551 | 0227 |  | Read Only | Phase A Total Output Energy_H | uint16_t | 10Wh
25 | 552 | 0228 |  | Read Only | Phase A Total Output Energy_L | uint16_t | 10Wh
26 | 553 | 0229
27 | 554 | 022A
28 | 555 | 022B
29 | 556 | 022C
30 | 557 | 022D
31 | 558 | 022E
32 | 559 | 022F
33 | 560 | 0230 |  | Read Only | Phase B Output Voltage | int16_t | 0.1V
34 | 561 | 0231 |  | Read Only | Phase B Output Frequency | int16_t | 0.01Hz
35 | 562 | 0232 |  | Read Only | Phase B Output Current | int16_t | 0.01A
36 | 563 | 0233 |  | Read Only | Phase B Output Low-Range Current | int16_t | 0.01A
37 | 564 | 0234 |  | Read Only | Phase B Output Active Power | int16_t | 1W
38 | 565 | 0235 |  | Read Only | Phase B Output Apparent Power | int16_t | 1W
39 | 566 | 0236
40 | 567 | 0237
41 | 568 | 0238 |  | Read Only | Phase B Load Percentage | int16_t | 0.1%
42 | 569 | 0239 |  | Read Only | Phase B Today's Output Energy_H | uint16_t | 10Wh
43 | 570 | 023A |  | Read Only | Phase B Today's Output Energy_L | uint16_t | 10Wh
44 | 571 | 023B |  | Read Only | Phase B This Month's Output Energy_H | uint16_t | 10Wh
45 | 572 | 023C |  | Read Only | Phase B This Month's Output Energy_L | uint16_t | 10Wh
46 | 573 | 023D |  | Read Only | Phase B This Year's Output Energy_H | uint16_t | 10Wh
47 | 574 | 023E |  | Read Only | Phase B This Year's Output Energy_L | uint16_t | 10Wh
48 | 575 | 023F |  | Read Only | Phase B Total Output Energy_H | uint16_t | 10Wh
49 | 576 | 0240 |  | Read Only | Phase B Total Output Energy_L | uint16_t | 10Wh
50 | 577 | 0241
51 | 578 | 0242
52 | 579 | 0243
53 | 580 | 0244
54 | 581 | 0245
55 | 582 | 0246
56 | 583 | 0247
57 | 584 | 0248 |  | Read Only | Phase C Output Voltage | int16_t | 0.1V
58 | 585 | 0249 |  | Read Only | Phase C Output Frequency | int16_t | 0.01Hz
59 | 586 | 024A |  | Read Only | Phase C Output Current | int16_t | 0.01A
60 | 587 | 024B |  | Read Only | Phase C Output Low-Range Current | int16_t | 0.01A
61 | 588 | 024C |  | Read Only | Phase C Output Active Power | int16_t | 1W
62 | 589 | 024D |  | Read Only | Phase C Output Apparent Power | int16_t | 1W
63 | 590 | 024E
64 | 591 | 024F
65 | 592 | 0250 |  | Read Only | Phase C Load Percentage | int16_t | 0.1%
66 | 593 | 0251 |  | Read Only | Phase C Today's Output Energy_H | uint16_t | 10Wh
67 | 594 | 0252 |  | Read Only | Phase C Today's Output Energy_L | uint16_t | 10Wh
68 | 595 | 0253 |  | Read Only | Phase C This Month's Output Energy_H | uint16_t | 10Wh
69 | 596 | 0254 |  | Read Only | Phase C This Month's Output Energy_L | uint16_t | 10Wh
70 | 597 | 0255 |  | Read Only | Phase C This Year's Output Energy_H | uint16_t | 10Wh
71 | 598 | 0256 |  | Read Only | Phase C This Year's Output Energy_L | uint16_t | 10Wh
72 | 599 | 0257 |  | Read Only | Phase C Total Output Energy_H | uint16_t | 10Wh
73 | 600 | 0258 |  | Read Only | Phase C Total Output Energy_L | uint16_t | 10Wh
74 | 601 | 0259
75 | 602 | 025A
76 | 603 | 025B
77 | 604 | 025C
78 | 605 | 025D
79 | 606 | 025E
80 | 607 | 025F

## WF_PV
No. | Address (Decimal) | Address | Variable Name | Permission | Meaning | Variable Type | Unit | Usage | Lower Limit | Upper Limit
| 608 | 0260 |  |  | Total PV Address Set
1 | 608 | 0260 |  | Read Only | Total PV Voltage | int16_t | 0.1V
2 | 609 | 0261 |  | Read Only | Total PV Current_H | int16_t | 0.01A
3 | 610 | 0262 |  | Read Only | Total PV Current_L | int16_t | 0.01A
4 | 611 | 0263 |  | Read Only | Total PV Power_H | int16_t | 1W
5 | 612 | 0264 |  | Read Only | Total PV Power_L | int16_t | 1W
6 | 613 | 0265 |  | Read Only | Total PV Tracking Status | int16_t
7 | 614 | 0266 |  | Read Only | Total PV Chargeable Status | int16_t
8 | 615 | 0267 |  | Read Only | Total PV Today's Generation_H | uint16_t | 10Wh
9 | 616 | 0268 |  | Read Only | Total PV Today's Generation_L | uint16_t | 10Wh
10 | 617 | 0269 |  | Read Only | Total PV This Month's Generation_H | uint16_t | 10Wh
11 | 618 | 026A |  | Read Only | Total PV This Month's Generation_L | uint16_t | 10Wh
12 | 619 | 026B |  | Read Only | Total PV This Year's Generation_H | uint16_t | 10Wh
13 | 620 | 026C |  | Read Only | Total PV This Year's Generation_L | uint16_t | 10Wh
14 | 621 | 026D |  | Read Only | Total PV Lifetime Generation_H | uint16_t | 10Wh
15 | 622 | 026E |  | Read Only | Total PV Lifetime Generation_L | uint16_t | 10Wh
16 | 623 | 026F
17 | 624 | 0270 |  | Read Only | PV1 Voltage | int16_t | 0.1V
18 | 625 | 0271 |  | Read Only | PV1 Current | int16_t | 0.01A
19 | 626 | 0272 |  | Read Only | PV1 Power | int16_t | 1W
20 | 627 | 0273 |  | Read Only | PV1 Tracking Status | int16_t
21 | 628 | 0274 |  | Read Only | PV1 Chargeable Status | int16_t
22 | 629 | 0275 |  | Read Only | PV1 Today's Generation_H | uint16_t | 10Wh
23 | 630 | 0276 |  | Read Only | PV1 Today's Generation_L | uint16_t | 10Wh
24 | 631 | 0277 |  | Read Only | PV1 This Month's Generation_H | uint16_t | 10Wh
25 | 632 | 0278 |  | Read Only | PV1 This Month's Generation_L | uint16_t | 10Wh
26 | 633 | 0279 |  | Read Only | PV1 This Year's Generation_H | uint16_t | 10Wh
27 | 634 | 027A |  | Read Only | PV1 This Year's Generation_L | uint16_t | 10Wh
28 | 635 | 027B |  | Read Only | PV1 Lifetime Generation_H | uint16_t | 10Wh
29 | 636 | 027C |  | Read Only | PV1 Lifetime Generation_L | uint16_t | 10Wh
30 | 637 | 027D
31 | 638 | 027E
32 | 639 | 027F
33 | 640 | 0280 |  | Read Only | PV2 Voltage | int16_t | 0.1V
34 | 641 | 0281 |  | Read Only | PV2 Current | int16_t | 0.01A
35 | 642 | 0282 |  | Read Only | PV2 Power | int16_t | 1W
36 | 643 | 0283 |  | Read Only | PV2 Tracking Status | int16_t
37 | 644 | 0284 |  | Read Only | PV2 Chargeable Status | int16_t
38 | 645 | 0285 |  | Read Only | PV2 Today's Generation_H | uint16_t | 10Wh
39 | 646 | 0286 |  | Read Only | PV2 Today's Generation_L | uint16_t | 10Wh
40 | 647 | 0287 |  | Read Only | PV2 This Month's Generation_H | uint16_t | 10Wh
41 | 648 | 0288 |  | Read Only | PV2 This Month's Generation_L | uint16_t | 10Wh
42 | 649 | 0289 |  | Read Only | PV2 This Year's Generation_H | uint16_t | 10Wh
43 | 650 | 028A |  | Read Only | PV2 This Year's Generation_L | uint16_t | 10Wh
44 | 651 | 028B |  | Read Only | PV2 Lifetime Generation_H | uint16_t | 10Wh
45 | 652 | 028C |  | Read Only | PV2 Lifetime Generation_L | uint16_t | 10Wh
46 | 653 | 028D
47 | 654 | 028E
48 | 655 | 028F
49 | 656 | 0290
50 | 657 | 0291
51 | 658 | 0292
52 | 659 | 0293
53 | 660 | 0294
54 | 661 | 0295
55 | 662 | 0296
56 | 663 | 0297
57 | 664 | 0298
58 | 665 | 0299
59 | 666 | 029A
60 | 667 | 029B
61 | 668 | 029C
62 | 669 | 029D
63 | 670 | 029E
64 | 671 | 029F

## WF_INV
No. | Address (Decimal) | Address | Variable Name | Permission | Meaning | Variable Type | Unit | Usage | Lower Limit | Upper Limit
| 672 | 02A0 |  |  | Inverter Address Set
1 | 672 | 02A0 |  | Read Only | Inverter Voltage Setpoint | int16_t | 0.1Hz
2 | 673 | 02A1 |  | Read Only | Inverter Frequency Setpoint | int16_t | 0.01Hz
3 | 674 | 02A2
4 | 675 | 02A3
5 | 676 | 02A4
6 | 677 | 02A5
7 | 678 | 02A6
8 | 679 | 02A7
9 | 680 | 02A8
10 | 681 | 02A9
11 | 682 | 02AA |  | Read Only | Phase A Inverter Voltage | int16_t | 0.1V
12 | 683 | 02AB |  | Read Only | Phase A Inverter Frequency | int16_t | 0.01Hz
13 | 684 | 02AC |  | Read Only | Phase A Inverter Current | int16_t | 0.01A
14 | 685 | 02AD |  | Read Only | Phase A DC Component | int16_t | 1mV
15 | 686 | 02AE |  | Read Only | Phase A Daily Input Energy_H | uint16_t | 10W
16 | 687 | 02AF |  | Read Only | Phase A Daily Input Energy_L | uint16_t | 10W
17 | 688 | 02B0 |  | Read Only | Phase A Monthly Input Energy_H | uint16_t | 10W
18 | 689 | 02B1 |  | Read Only | Phase A Monthly Input Energy_L | uint16_t | 10W
19 | 690 | 02B2 |  | Read Only | Phase A Total Input Energy_H | uint16_t | 10W
20 | 691 | 02B3 |  | Read Only | Phase A Total Input Energy_L | uint16_t | 10W
21 | 692 | 02B4 |  | Read Only | Phase A Daily Output Energy_H | uint16_t | 10W
22 | 693 | 02B5 |  | Read Only | Phase A Daily Output Energy_L | uint16_t | 10W
23 | 694 | 02B6 |  | Read Only | Phase A Monthly Output Energy_H | uint16_t | 10W
24 | 695 | 02B7 |  | Read Only | Phase A Monthly Output Energy_L | uint16_t | 10W
25 | 696 | 02B8 |  | Read Only | Phase A Total Output Energy_H | uint16_t | 10W
26 | 697 | 02B9 |  | Read Only | Phase A Total Output Energy_L | uint16_t | 10W
27 | 698 | 02BA |  | Read Only | Phase B Inverter Voltage | int16_t | 0.1V
28 | 699 | 02BB |  | Read Only | Phase B Inverter Frequency | int16_t | 0.01Hz
29 | 700 | 02BC |  | Read Only | Phase B Inverter Current | int16_t | 0.01A
30 | 701 | 02BD |  | Read Only | Phase B DC Component | int16_t | 1mV
31 | 702 | 02BE
32 | 703 | 02BF
33 | 704 | 02C0 |  | Read Only | Phase B Daily Grid Feed-in Energy_H | uint16_t | 10W
34 | 705 | 02C1 |  | Read Only | Phase B Daily Grid Feed-in Energy_L | uint16_t | 10W
35 | 706 | 02C2 |  | Read Only | Phase B Monthly Grid Feed-in Energy_H | uint16_t | 10W
36 | 707 | 02C3 |  | Read Only | Phase B Monthly Grid Feed-in Energy_L | uint16_t | 10W
37 | 708 | 02C4 |  | Read Only | Phase B Total Grid Feed-in Energy_H | uint16_t | 10W
38 | 709 | 02C5 |  | Read Only | Phase B Total Grid Feed-in Energy_L | uint16_t | 10W
39 | 710 | 02C6
40 | 711 | 02C7
41 | 712 | 02C8
42 | 713 | 02C9
43 | 714 | 02CA |  | Read Only | Phase C Inverter Voltage | int16_t | 0.1V
44 | 715 | 02CB |  | Read Only | Phase C Inverter Frequency | int16_t | 0.01Hz
45 | 716 | 02CC |  | Read Only | Phase C Inverter Current | int16_t | 0.01A
46 | 717 | 02CD |  | Read Only | Phase C DC Component | int16_t | 1mV
47 | 718 | 02CE
48 | 719 | 02CF
49 | 720 | 02D0 |  | Read Only | Phase C Daily Grid Feed-in Energy_H | uint16_t | 10W
50 | 721 | 02D1 |  | Read Only | Phase C Daily Grid Feed-in Energy_L | uint16_t | 10W
51 | 722 | 02D2 |  | Read Only | Phase C Monthly Grid Feed-in Energy_H | uint16_t | 10W
52 | 723 | 02D3 |  | Read Only | Phase C Monthly Grid Feed-in Energy_L | uint16_t | 10W
53 | 724 | 02D4 |  | Read Only | Phase C Total Grid Feed-in Energy_H | uint16_t | 10W
54 | 725 | 02D5 |  | Read Only | Phase C Total Grid Feed-in Energy_L | uint16_t | 10W
55 | 726 | 02D6
56 | 727 | 02D7
57 | 728 | 02D8
58 | 729 | 02D9
59 | 730 | 02DA
60 | 731 | 02DB
61 | 732 | 02DC
62 | 733 | 02DD
63 | 734 | 02DE
64 | 735 | 02DF

## WF_FAN
No. | Address (Decimal) | Address | Variable Name | Permission | Meaning | Variable Type | Unit | Usage | Lower Limit | Upper Limit
| 800 | 0320 |  |  | Fan Info Address Set
1 | 800 | 0320 |  | Read Only | Fan Speed |  | %
2 | 801 | 0321 |  | Read Only | Fan Status |  |  | Non-zero indicates fan locked/stalled
3 | 802 | 0322
4 | 803 | 0323

## WF_NTC
No. | Address (Decimal) | Address | Variable Name | Permission | Meaning | Variable Type | Unit | Usage | Lower Limit | Upper Limit
| 816 | 0330 |  |  | Temperature Address Set
1 | 816 | 0330 |  | Read Only | PV Temperature |  | ℃
2 | 817 | 0331 |  | Read Only | Inverter Temperature |  | ℃
3 | 818 | 0332 |  | Read Only | Charger Temperature |  | ℃
4 | 819 | 0333 |  | Read Only | Charger 2 Temperature |  | ℃
5 | 820 | 0334 |  | Read Only | Ambient Temperature |  | ℃
6 | 821 | 0335 |  | Read Only | Discharge Temperature |  | ℃
7 | 822 | 0336
8 | 823 | 0337
9 | 824 | 0338
10 | 825 | 0339
11 | 826 | 033A
12 | 827 | 033B
13 | 828 | 033C
14 | 829 | 033D
15 | 830 | 033E
16 | 831 | 033F

## WF_FunctionSwitch
No. | Address (Decimal) | Address | Variable Name | Permission | Meaning | Variable Type | Unit | Usage | Lower Limit | Upper Limit
| 848 | 0350 |  |  | Special Function Switch Address Set
1 | 848 | 0350 |  | Read Only | Resettable Factory Setting Function 0_H |  | BIT00: Enable SOC switch to grid BIT01: Enable SOC switch to battery BIT02: Enable SOC low-voltage shutdown BIT03: Dual output unlimited time BIT04: BMS ID auto search BIT05: BMS ID full sampling/oversampling BIT06: Reserved BIT07: Auto backlight off BIT08: Generator enable
2 | 849 | 0351 |  | Read Only | Resettable Factory Setting Function 0_L |  | BIT00: LCD auto-return to default display page on timeout BIT01: Restart on over temperature BIT02: Restart on overload BIT03: Switch to bypass on overload BIT04: Low power-consumption power saving BIT05: Auto grid frequency detection BIT06: Inverter soft-start after output relay closes BIT07: Battery open-circuit warning BIT08: Enable equalization charging mode BIT09: Reserved BIT10: Grid feed-in function enable BIT11: Buzzer mute BIT12: Dual output function enable BIT13: Default return to main screen setting BIT14: Main input change warning BIT15: Parallel ID auto search
3 | 850 | 0352 |  | Read Only | Resettable Factory Setting Function 1_H |  | Reserved
4 | 851 | 0353 |  | Read Only | Resettable Factory Setting Function 1_L |  | Reserved
5 | 852 | 0354 |  | Read Only | Non-Resettable Factory Setting Function 0_H |  | Reserved
6 | 853 | 0355 |  | Read Only | Non-Resettable Factory Setting Function 0_L |  | Reserved
7 | 854 | 0356 |  | Read Only | Non-Resettable Factory Setting Function 1_H |  | Reserved
8 | 855 | 0357 |  | Read Only | Non-Resettable Factory Setting Function 1_L |  | Reserved
9 | 856 | 0358
10 | 857 | 0359
11 | 858 | 035A
12 | 859 | 035B
13 | 860 | 035C
14 | 861 | 035D
15 | 862 | 035E
16 | 863 | 035F

## WF_Time
No. | Address (Decimal) | Address | Variable Name | Permission | Meaning | Variable Type | Unit | Usage | Lower Limit | Upper Limit
| 864 | 0360 |  |  | Time Address Set
1 | 864 | 0360 |  | Read Only | Year
2 | 865 | 0361 |  | Read Only | Month
3 | 866 | 0362 |  | Read Only | Day
4 | 867 | 0363 |  | Read Only | Hour
5 | 868 | 0364 |  | Read Only | Minute
6 | 869 | 0365 |  | Read Only | Second
7 | 870 | 0366
8 | 871 | 0367

## WF_PARA
No. | Address (Decimal) | Address | Variable Name | Permission | Meaning | Variable Type | Unit | Usage | Lower Limit | Upper Limit
| 1024 | 0400
1 | 1024 | 0400

## WF_Admin
No. | Address (Decimal) | Address | Variable Name | Permission | Meaning | Variable Type | Unit | Usage | Lower Limit | Upper Limit
| 4096 | 1000 |  |  | Settings & Configuration
1 | 4096 | 1000 |  | Read/Write | Restore Factory Settings |  |  | Write 1 to restore to customer-customized settings
2 | 4097 | 1001 |  | Read/Write | Restore Factory Settings |  |  | Write 1 to clear customer-customized settings
3 | 4098 | 1002 |  | Read/Write | Restore Factory Settings |  |  | Write 1 to clear calibration information
4 | 4099 | 1003 |  | Read/Write | SN Write |  |  | Write 1 to save SN into memory
5 | 4100 | 1004
6 | 4101 | 1005
7 | 4102 | 1006
8 | 4103 | 1007
9 | 4104 | 1008
10 | 4105 | 1009 |  | Read/Write |  |  |  | User mode: 0x0000 Admin mode: 0x0001
11 | 4106 | 100A |  | Read/Write | Admin Account |  |  | Default (not set) is User, which has only query permission and permission to set some parameters Admin can set calibration values (FCT requires admin login) Admin account: 0x0010 Admin password: 0x1C1A
12 | 4107 | 100B |  | Read/Write | Admin Password
13 | 4108 | 100C |  | Read/Write | Authorization Duration |  | s | 0xFFFF: Permanent authorization
14 | 4109 | 100D
15 | 4110 | 100E
16 | 4111 | 100F
17 | 4112 | 1010
18 | 4113 | 1011
19 | 4114 | 1012
20 | 4115 | 1013
21 | 4116 | 1014
22 | 4117 | 1015
23 | 4118 | 1016
24 | 4119 | 1017
25 | 4120 | 1018
26 | 4121 | 1019
27 | 4122 | 101A
28 | 4123 | 101B
29 | 4124 | 101C
30 | 4125 | 101D
31 | 4126 | 101E
32 | 4127 | 101F
33 | 4128 | 1020 |  | Read Only | SN Code | uint16_t
34 | 4129 | 1021 |  | Read Only | SN Code | uint16_t
35 | 4130 | 1022 |  | Read Only | SN Code | uint16_t
36 | 4131 | 1023 |  | Read Only | SN Code | uint16_t
37 | 4132 | 1024 |  | Read Only | SN Code | uint16_t
38 | 4133 | 1025 |  | Read Only | SN Code | uint16_t
39 | 4134 | 1026 |  | Read Only | SN Code | uint16_t
40 | 4135 | 1027 |  | Read Only | SN Code | uint16_t
41 | 4136 | 1028 |  | Read Only | SN Code | uint16_t
42 | 4137 | 1029 |  | Read Only | SN Code | uint16_t
43 | 4138 | 102A |  | Read Only | SN Code | uint16_t
44 | 4139 | 102B |  | Read Only | SN Code | uint16_t
45 | 4140 | 102C |  | Read Only | SN Code | uint16_t
46 | 4141 | 102D |  | Read Only | SN Code | uint16_t
47 | 4142 | 102E |  | Read Only | SN Code | uint16_t

## WF_FCT
No. | Address (Decimal) | Address | Variable Name | Permission | Meaning | Variable Type | Unit | Usage | Lower Limit | Upper Limit
| 4352 | 1100
1 | 4352 | 1100 |  | Read/Write | FCT Mode |  |  | 0: Non-test mode 1: Drive test mode
2 | 4353 | 1101 |  | Read/Write | Drive Enable | Bit |  | 0x0000: Off 0x0001: Discharge 0x0002: Charge 0x0004: PFC drive 0x0008: Inverter drive 0x0010: PV drive 0x0020: L-line relay drive 0x0040: N-line relay drive 0x0080: Output relay drive 0x0100: Auxiliary relay drive 0x0200: L-line SCR 0x0400: Output SCR 0x0800: Dry contact 1 0x1000: Dry contact 2
3 | 4354 | 1102 |  | Read/Write | Discharge Drive Percentage |  | 0.01%
4 | 4355 | 1103 |  | Read/Write | Charge Drive Percentage |  | 0.01%
5 | 4356 | 1104 |  | Read/Write | Inverter Drive Percentage |  | 0.01%
6 | 4357 | 1105 |  | Read/Write | PV Drive Percentage |  | 0.01%
7 | 4358 | 1106 |  | Read/Write | Relay Status |  |  | BIT0: BIT1: BIT2:
8 | 4359 | 1107 |  | Read/Write | SCR Status |  |  | BIT0: BIT1: BIT2:
9 | 4360 | 1108 |  | Read/Write | Fan Drive Percentage |  | %
10 | 4361 | 1109 |  | Read/Write | Dry Contact Switch
11 | 4362 | 110A |  | Read/Write | Buzzer Switch
12 | 4363 | 110B |  | Read/Write | Factory Test Accelerated Entry into Charging State Switch |  |  | 0: Normal mode 1: Factory test mode, skips battery-not-connected detection to accelerate entry into grid charging state
13 | 4364 | 110C |  | Read/Write | Button Status |  |  | BIT0: Up button pressed BIT1: Down button pressed BIT2: Confirm button pressed BIT3: Back button pressed Starting from the first button press, this bit clears after 10s
14 | 4365 | 110D
15 | 4366 | 110E
16 | 4367 | 110F
17 | 4368 | 1110
18 | 4369 | 1111
19 | 4370 | 1112

## WF_Calibration
No. | Address (Decimal) | Address | Variable Name | Permission | Meaning | Variable Type | Unit | Usage | Lower Limit | Upper Limit | Calibration Object Table
| 4608 | 1200 |  |  | Calibration Information | [5 empty] | Decimal | Hexadecimal | Object Name | Measurement Unit | Inverter Reading Address (H)
1 | 4608 | 1200 |  | Read/Write | Object |  | uint16 |  |  |  | 1 | 0x0001 | Grid Voltage | 0.1V | 01B0
2 | 4609 | 1201 |  | Read/Write | Calibration Method |  | uint16 | 0: Single-point calibration 1: Two-point calibration 2: Restore factory settings |  |  | 2 | 0x0002 | Grid Current | 0.01A | 01B1
3 | 4610 | 1202 |  | Read/Write | External Measurement 1 |  | int16_t |  |  |  | 3 | 0x0003 | Grid Power | 1W | /
4 | 4611 | 1203 |  | Read/Write | Internal Measurement 1 |  | int16_t |  |  |  | 4 | 0x0004 | Grid Leakage Current | 0.01A | /
5 | 4612 | 1204 |  | Read/Write | External Measurement 2 |  | int16_t |  |  |  | 5 | 0x0005 | Generator Voltage | 0.1V | 2000
6 | 4613 | 1205 |  | Read/Write | Internal Measurement 2 |  | int16_t |  |  |  | 6 | 0x0006 | Generator Current | 0.01A | 2001
7 | 4614 | 1206 |  |  | Reserved | [5 empty] | 7 | 0x0007 | Generator Power | 1W | /
8 | 4615 | 1207 |  |  | Reserved | [5 empty] | 8 | 0x0008 | Inverter Voltage | 0.1V | 02AA
9 | 4616 | 1208 |  | Read/Write | Time Calibration Enable |  | int16_t | 0: Waiting/Completed 1: Calibrate 2: Reset |  |  | 9 | 0x0009 | Inverter DC Component | 1mV | 02AD
10 | 4617 | 1209 |  | Read/Write | Year Calibration |  | int16_t |  |  |  | 10 | 0x000A | Inverter Current | 0.01A | 02AC
11 | 4618 | 120A |  | Read/Write | Month Calibration |  | int16_t |  |  |  | 11 | 0x000B | Inverter Low-Range Current | 0.01A | /
12 | 4619 | 120B |  | Read/Write | Week Calibration |  | int16_t |  |  |  | 12 | 0x000C | Inverter Low-Range Power | 1W | /
13 | 4620 | 120C |  | Read/Write | Day Calibration |  | int16_t |  |  |  | 13 | 0x000D | Inverter Power | 1W | /
14 | 4621 | 120D |  | Read/Write | Hour Calibration |  | int16_t |  |  |  | 14 | 0x000E | Output Voltage | 0.1V | 0218
15 | 4622 | 120E |  | Read/Write | Minute Calibration |  | int16_t |  |  |  | 15 | 0x000F | Output Current | 0.01A | 021A
16 | 4623 | 120F |  | Read/Write | Second Calibration |  | int16_t |  |  |  | 16 | 0x0010 | Output Power | 1W | 021D
17 | 4624 | 1210 | [8 empty] | 17 | 0x0011 | PV1 Voltage | 0.1V | 0270
18 | 4625 | 1211 | [8 empty] | 18 | 0x0012 | PV1 Current | 0.01A | 0271
19 | 4626 | 1212 | [8 empty] | 19 | 0x0013 | PV1 Power | 1W | 0272
20 | 4627 | 1213 | [8 empty] | 20 | 0x0014 | PV2 Voltage | 0.1V | /
21 | 4628 | 1214 | [8 empty] | 21 | 0x0015 | PV2 Current | 0.01A | /
22 | 4629 | 1215 | [8 empty] | 22 | 0x0016 | PV2 Power | 1W | /
23 | 4630 | 1216 | [8 empty] | 23 | 0x0017 | Bus Voltage | 0.1V | /
24 | 4631 | 1217 | [8 empty] | 24 | 0x0018 | Battery Voltage | 0.1V | 0155
25 | 4632 | 1218 | [8 empty] | 25 | 0x0019 | Battery Current | 0.1A | 0157
26 | 4633 | 1219 | [8 empty] | 26 | 0x001A | Battery Power | 1W | /
27 | 4634 | 121A
28 | 4635 | 121B | [8 empty] | 23767 | 0x7FFF | Select All (used to clear calibration)
29 | 4636 | 121C
30 | 4637 | 121D
31 | 4638 | 121E
32 | 4639 | 121F

## WF_Generator
No. | Address (Decimal) | Address | Variable Name | Permission | Meaning | Variable Type | Unit | Usage | Lower Limit | Upper Limit
| 8192 | 2000 |  |  | Generator Status Debug Address Set
1 | 8192 | 2000 |  | Read Only | Phase A Generator Voltage | int16_t | 0.1V
2 | 8193 | 2001 |  | Read Only | Phase A Generator Current | int16_t | 0.01A
3 | 8194 | 2002 |  | Read Only | Phase A Generator Frequency | int16_t | 0.01Hz
4 | 8195 | 2003 |  | Read Only | Phase A Generator Power | int16_t | 10W
5 | 8196 | 2004
6 | 8197 | 2005
7 | 8198 | 2006
8 | 8199 | 2007
9 | 8200 | 2008
10 | 8201 | 2009
11 | 8202 | 200A
12 | 8203 | 200B
13 | 8204 | 200C
14 | 8205 | 200D
15 | 8206 | 200E
16 | 8207 | 200F

## WF_OTA
No. | Address (Decimal) | Address | Variable Name | Permission | Meaning | Variable Type | Unit | Usage | Lower Limit | Upper Limit
| 16384 | 4000 |  |  | Upgrade Command & Data
1 | 16384 | 4000 |  |  | Upgrade Command Code | uint16_t |  | Command type / Bit0-Bit7 Software type / Bit8-Bit15 Command type: ID Value Description 0x00 Activate command, instructs BOOT to jump to APP after loading completes 0x01 Jump command, instructs APP to jump to BOOT at start of loading 0x02 Erase command, instructs FLASH erase during loading 0x20 Use default communication baud rate (no setting needed) 0x21 Set communication baud rate to 9600bps 0x22 Set communication baud rate to 38400bps 0x23 Set communication baud rate to 115200bps 0x24 Set communication baud rate to 312500bps Software type: ID Value Description 0x00 Upgrade EMS software code 0x01 Upgrade PCS software code 0x02 Upgrade BMS software code 0x03 Upgrade MCU software code 0x10 Upgrade EMS bootloader code (reserved) 0x11 Upgrade PCS bootloader code (reserved) 0x12 Upgrade BMS bootloader code (reserved) 0x13 Upgrade MCU bootloader code (reserved)
2 | 16385 | 4001 |  |  | Upgrade Data | uint16_t |  | Pack ID
3 | 16386 | 4002 |  |  | Upgrade Data | uint16_t |  | Upgrade data must be 32-bit aligned! Otherwise the chip's Flash write will fail
4 | 16387 | 4003 |  |  | Upgrade Data | uint16_t
5 | 16388 | 4004 |  |  | Upgrade Data | uint16_t
6 | 16389 | 4005 |  |  | Upgrade Data | uint16_t
7 | 16390 | 4006 |  |  | Upgrade Data | uint16_t
8 | 16391 | 4007 |  |  | Upgrade Data | uint16_t
9 | 16392 | 4008 |  |  | Upgrade Data | uint16_t
10 | 16393 | 4009 |  |  | Upgrade Data | uint16_t
11 | 16394 | 400A |  |  | Upgrade Data | uint16_t
12 | 16395 | 400B |  |  | Upgrade Data | uint16_t
13 | 16396 | 400C |  |  | Upgrade Data | uint16_t
14 | 16397 | 400D |  |  | Upgrade Data | uint16_t
15 | 16398 | 400E |  |  | Upgrade Data | uint16_t
16 | 16399 | 400F |  |  | Upgrade Data | uint16_t
17 | 16400 | 4010 |  |  | Upgrade Data | uint16_t
18 | 16401 | 4011 |  |  | Upgrade Data | uint16_t
19 | 16402 | 4012 |  |  | Upgrade Data | uint16_t
20 | 16403 | 4013 |  |  | Upgrade Data | uint16_t
21 | 16404 | 4014 |  |  | Upgrade Data | uint16_t
22 | 16405 | 4015 |  |  | Upgrade Data | uint16_t
23 | 16406 | 4016 |  |  | Upgrade Data | uint16_t
24 | 16407 | 4017 |  |  | Upgrade Data | uint16_t
25 | 16408 | 4018 |  |  | Upgrade Data | uint16_t
26 | 16409 | 4019 |  |  | Upgrade Data | uint16_t
27 | 16410 | 401A |  |  | Upgrade Data | uint16_t
28 | 16411 | 401B |  |  | Upgrade Data | uint16_t
29 | 16412 | 401C |  |  | Upgrade Data | uint16_t
30 | 16413 | 401D |  |  | Upgrade Data | uint16_t
31 | 16414 | 401E |  |  | Upgrade Data | uint16_t
32 | 16415 | 401F |  |  | Upgrade Data | uint16_t
33 | 16416 | 4020 |  |  | Upgrade Data | uint16_t
34 | 16417 | 4021 |  |  | Upgrade Data | uint16_t
35 | 16418 | 4022 |  |  | Upgrade Data | uint16_t
36 | 16419 | 4023 |  |  | Upgrade Data | uint16_t
37 | 16420 | 4024 |  |  | Upgrade Data | uint16_t
38 | 16421 | 4025 |  |  | Upgrade Data | uint16_t
39 | 16422 | 4026 |  |  | Upgrade Data | uint16_t
40 | 16423 | 4027 |  |  | Upgrade Data | uint16_t
41 | 16424 | 4028 |  |  | Upgrade Data | uint16_t
42 | 16425 | 4029 |  |  | Upgrade Data | uint16_t
43 | 16426 | 402A |  |  | Upgrade Data | uint16_t
44 | 16427 | 402B |  |  | Upgrade Data | uint16_t
45 | 16428 | 402C |  |  | Upgrade Data | uint16_t
46 | 16429 | 402D |  |  | Upgrade Data | uint16_t
47 | 16430 | 402E |  |  | Upgrade Data | uint16_t
48 | 16431 | 402F |  |  | Upgrade Data | uint16_t
49 | 16432 | 4030 |  |  | Upgrade Data | uint16_t
50 | 16433 | 4031 |  |  | Upgrade Data | uint16_t
51 | 16434 | 4032 |  |  | Upgrade Data | uint16_t
52 | 16435 | 4033 |  |  | Upgrade Data | uint16_t
53 | 16436 | 4034 |  |  | Upgrade Data | uint16_t
54 | 16437 | 4035 |  |  | Upgrade Data | uint16_t
55 | 16438 | 4036 |  |  | Upgrade Data | uint16_t
56 | 16439 | 4037 |  |  | Upgrade Data | uint16_t
57 | 16440 | 4038 |  |  | Upgrade Data | uint16_t
58 | 16441 | 4039 |  |  | Upgrade Data | uint16_t
59 | 16442 | 403A |  |  | Upgrade Data | uint16_t
60 | 16443 | 403B |  |  | Upgrade Data | uint16_t
61 | 16444 | 403C |  |  | Upgrade Data | uint16_t
62 | 16445 | 403D |  |  | Upgrade Data | uint16_t
63 | 16446 | 403E |  |  | Upgrade Data | uint16_t
64 | 16447 | 403F |  |  | Upgrade Data | uint16_t
65 | 16448 | 4040 |  |  | Upgrade Data | uint16_t
66 | 16449 | 4041 |  |  | Upgrade Data | uint16_t
67 | 16450 | 4042 |  |  | Upgrade Data | uint16_t
68 | 16451 | 4043 |  |  | Upgrade Data | uint16_t
69 | 16452 | 4044 |  |  | Upgrade Data | uint16_t
70 | 16453 | 4045 |  |  | Upgrade Data | uint16_t
71 | 16454 | 4046 |  |  | Upgrade Data | uint16_t
72 | 16455 | 4047 |  |  | Upgrade Data | uint16_t
73 | 16456 | 4048 |  |  | Upgrade Data | uint16_t
74 | 16457 | 4049 |  |  | Upgrade Data | uint16_t
75 | 16458 | 404A |  |  | Upgrade Data | uint16_t
76 | 16459 | 404B |  |  | Upgrade Data | uint16_t
77 | 16460 | 404C |  |  | Upgrade Data | uint16_t
78 | 16461 | 404D |  |  | Upgrade Data | uint16_t
79 | 16462 | 404E |  |  | Upgrade Data | uint16_t
80 | 16463 | 404F |  |  | Upgrade Data | uint16_t
81 | 16464 | 4050 |  |  | Upgrade Data | uint16_t
82 | 16465 | 4051 |  |  | Upgrade Data | uint16_t
83 | 16466 | 4052 |  |  | Upgrade Data | uint16_t
84 | 16467 | 4053 |  |  | Upgrade Data | uint16_t
85 | 16468 | 4054 |  |  | Upgrade Data | uint16_t
86 | 16469 | 4055 |  |  | Upgrade Data | uint16_t
87 | 16470 | 4056 |  |  | Upgrade Data | uint16_t
88 | 16471 | 4057 |  |  | Upgrade Data | uint16_t
89 | 16472 | 4058 |  |  | Upgrade Data | uint16_t
90 | 16473 | 4059 |  |  | Upgrade Data | uint16_t
91 | 16474 | 405A |  |  | Upgrade Data | uint16_t
92 | 16475 | 405B |  |  | Upgrade Data | uint16_t
93 | 16476 | 405C |  |  | Upgrade Data | uint16_t
94 | 16477 | 405D |  |  | Upgrade Data | uint16_t
95 | 16478 | 405E |  |  | Upgrade Data | uint16_t
96 | 16479 | 405F |  |  | Upgrade Data | uint16_t
97 | 16480 | 4060 |  |  | Upgrade Data | uint16_t
98 | 16481 | 4061 |  |  | Upgrade Data | uint16_t
99 | 16482 | 4062 |  |  | Upgrade Data | uint16_t
100 | 16483 | 4063 |  |  | Upgrade Data | uint16_t
101 | 16484 | 4064 |  |  | Upgrade Data | uint16_t
102 | 16485 | 4065 |  |  | Upgrade Data | uint16_t
103 | 16486 | 4066 |  |  | Upgrade Data | uint16_t
104 | 16487 | 4067 |  |  | Upgrade Data | uint16_t
105 | 16488 | 4068 |  |  | Upgrade Data | uint16_t
106 | 16489 | 4069 |  |  | Upgrade Data | uint16_t
107 | 16490 | 406A |  |  | Upgrade Data | uint16_t
108 | 16491 | 406B |  |  | Upgrade Data | uint16_t
109 | 16492 | 406C |  |  | Upgrade Data | uint16_t
110 | 16493 | 406D |  |  | Upgrade Data | uint16_t
111 | 16494 | 406E |  |  | Upgrade Data | uint16_t
112 | 16495 | 406F |  |  | Upgrade Data | uint16_t
113 | 16496 | 4070 |  |  | Upgrade Data | uint16_t
114 | 16497 | 4071 |  |  | Upgrade Data | uint16_t
115 | 16498 | 4072 |  |  | Upgrade Data | uint16_t
116 | 16499 | 4073 |  |  | Upgrade Data | uint16_t
117 | 16500 | 4074 |  |  | Upgrade Data | uint16_t
118 | 16501 | 4075 |  |  | Upgrade Data | uint16_t
119 | 16502 | 4076 |  |  | Upgrade Data | uint16_t
120 | 16503 | 4077 |  |  | Upgrade Data | uint16_t
121 | 16504 | 4078 |  |  | Upgrade Data | uint16_t
122 | 16505 | 4079 |  |  | Upgrade Data | uint16_t
123 | 16506 | 407A |  |  | Upgrade Data | uint16_t
124 | 16507 | 407B |  |  | Upgrade Data | uint16_t
125 | 16508 | 407C |  |  | Upgrade Data | uint16_t
126 | 16509 | 407D |  |  | Upgrade Data | uint16_t
127 | 16510 | 407E |  |  | Upgrade Data | uint16_t
128 | 16511 | 407F |  |  | Upgrade Data | uint16_t
129 | 16512 | 4080 |  |  | Upgrade Data | uint16_t
130 | 16513 | 4081
131 | 16514 | 4082
132 | 16515 | 4083
133 | 16516 | 4084
134 | 16517 | 4085
135 | 16518 | 4086
136 | 16519 | 4087
137 | 16520 | 4088
138 | 16521 | 4089
139 | 16522 | 408A
140 | 16523 | 408B
141 | 16524 | 408C
142 | 16525 | 408D
143 | 16526 | 408E
144 | 16527 | 408F
145 | 16528 | 4090 |  |  | Upgrade Status | uint16_t |  | Bit0-Bit3 EMS upgrade status Bit4-Bit7 PCS upgrade status Bit8-Bit11 BMS upgrade status (reserved) Bit12-Bit15 MCU upgrade status (reserved) 0x00 Operation successful 0x01 FLASH write failed 0x02 FLASH write error, i.e. written content does not match read-back content 0x03 FLASH erase failed 0x04 Unsupported software, i.e. software/hardware mismatch 0x05 Software ID error 0x06 Received frame length does not match the length specified in the software header 0x07 Software body length error / total frame count received exceeds the max frame count allowed in the App region
146 | 16529 | 4091
147 | 16530 | 4092 |  |  | Running Status | uint16_t |  | Bit0-Bit3 EMS running status Bit4-Bit7 PCS running status Bit8-Bit11 BMS running status (reserved) Bit12-Bit15 MCU running status (reserved) ID Value Description 0x00 Running in APP region 0x01 Running in BOOT region 0x02 Upgrading 0x03 Upgrade failed
148 | 16531 | 4093
149 | 16532 | 4094 |  |  | Host Computer Flashing Status Setting | uint16_t |  | 0x00: Idle 0x01: Flashing in progress 0x02: Flashing complete
150 | 16533 | 4095 |  |  | This Packet's Device Type | uint16_t |  | BIT0:PCS BIT1:EMS BIT2:BMS BIT3:COM
151 | 16534 | 4096 |  |  | Flashable Type | uint16_t |  | BIT0:PCS BIT1:EMS BIT2:BMS BIT3:COM
152 | 16535 | 4097 |  |  | Model | uint16_t |  | 0x00:NULL 0x01:3K 0x02:5K 0x03:6K 0x04:11K
153 | 16536 | 4098 |  |  | Software Type | uint16_t |  | 0x00:ERROR 0x01:APP 0x02:BOOT
154 | 16537 | 4099 |  |  | Erase Time | uint16_t |  | Unit: ms
155 | 16538 | 409A |  |  | Reserved | uint16_t
156 | 16539 | 409B |  |  | Version Number_H | uint16_t
157 | 16540 | 409C |  |  | Version Number_L | uint16_t
158 | 16541 | 409D |  |  | Footprint_A | uint16_t
159 | 16542 | 409E |  |  | Footprint_B | uint16_t
160 | 16543 | 409F |  |  | Footprint_C | uint16_t
161 | 16544 | 40A0 |  |  | Footprint_D | uint16_t
162 | 16545 | 40A1 |  |  | Flash Packet Length_H
163 | 16546 | 40A2 |  |  | Flash Packet Length_L
164 | 16547 | 40A3
165 | 16548 | 40A4
166 | 16549 | 40A5
167 | 16550 | 40A6
168 | 16551 | 40A7
169 | 16552 | 40A8
170 | 16553 | 40A9
171 | 16554 | 40AA
172 | 16555 | 40AB
173 | 16556 | 40AC
174 | 16557 | 40AD
175 | 16558 | 40AE
176 | 16559 | 40AF
177 | 16560 | 40B0
178 | 16561 | 40B1
179 | 16562 | 40B2
180 | 16563 | 40B3
181 | 16564 | 40B4
182 | 16565 | 40B5
183 | 16566 | 40B6
184 | 16567 | 40B7
185 | 16568 | 40B8
186 | 16569 | 40B9
187 | 16570 | 40BA
188 | 16571 | 40BB
189 | 16572 | 40BC
190 | 16573 | 40BD
191 | 16574 | 40BE
192 | 16575 | 40BF
193 | 16576 | 40C0
194 | 16577 | 40C1
195 | 16578 | 40C2
196 | 16579 | 40C3
197 | 16580 | 40C4
198 | 16581 | 40C5
199 | 16582 | 40C6
200 | 16583 | 40C7
201 | 16584 | 40C8
202 | 16585 | 40C9
203 | 16586 | 40CA
204 | 16587 | 40CB
205 | 16588 | 40CC
206 | 16589 | 40CD
207 | 16590 | 40CE
208 | 16591 | 40CF
209 | 16592 | 40D0
210 | 16593 | 40D1
211 | 16594 | 40D2
212 | 16595 | 40D3
213 | 16596 | 40D4
214 | 16597 | 40D5
215 | 16598 | 40D6
216 | 16599 | 40D7
217 | 16600 | 40D8
218 | 16601 | 40D9

## WF_UserSet
No. | Address (Decimal) | Address | Variable Name | Permission | Meaning | Variable Type | Unit | Usage | Lower Limit | Upper Limit
| 16640 | 4100 |  |  | User Settings |  |  | Note: Only one parameter can be set per write to this setting field The host computer must ensure the value written is within the correct range, otherwise system function may be abnormal The interval between two settings should be greater than 500ms Default display of -1/65535 indicates a successful setting or that it is not currently in a setting state; if -1/65535 is read back after a write, the setting was successful
1 | 16640 | 4100 |  | Read/Write | Output Voltage | uint16_t | / | 0:208V 1:220V 2:230V 3:240V
2 | 16641 | 4101 |  | Read/Write | Output Frequency | uint16_t | / | 0:50Hz 1:60Hz
3 | 16642 | 4102 |  | Read/Write | Output Priority | uint16_t | / | 0:GPB 1:PGB 2:PBG 3:MKS
4 | 16643 | 4103 |  | Read/Write | Operating Mode | uint16_t | / | 0:APP 1:UPS
5 | 16644 | 4104 |  | Read/Write | Charge Priority | uint16_t | / | 0:PNG 1:OPV 2:PVF
6 | 16645 | 4105 |  | Read/Write | Grid Charge Current | uint16_t | 1A | Continuously adjustable 2-120A [VMH6KU only supports: 0x02: 2A 0x0A: 10A 0x14: 20A 0x1E: 30A 0x28: 40A 0x32: 50A 0x3C: 60A 0x46: 70A 0x50: 80A 0x5A: 90A 0x64: 100A 0x6E: 110A 0x78: 120A]
7 | 16646 | 4106 |  | Read/Write | Max Charge Current | uint16_t | / | 0:2A 1:10A 2:20A 3:30A 4:40A 5:50A 6:60A 7:70A 8:80A 9:90A 10:100A 11:110A 12:120A
8 | 16647 | 4107 |  | Read/Write | Battery Type | uint16_t | / | 0: Lead-acid battery 1: Flooded battery 2: Ternary lithium (NMC) battery 3: LiFePO4 battery 4: User-defined battery
9 | 16648 | 4108 |  | Read/Write | Battery Low Voltage Point | uint16_t | 0.1V | Lead-acid/Flooded: 44V, not adjustable NMC/LiFePO4: 41.2V-50V Custom: 42V-54V
10 | 16649 | 4109 |  | Read/Write | Battery Undervoltage Point (Battery Shutdown Point) | uint16_t | 0.1V | Lead-acid/Flooded: 42V, not adjustable NMC/LiFePO4/Custom: 40V-48V
11 | 16650 | 410A |  | Read/Write | Constant Voltage Point | uint16_t | 0.1V | Lead-acid: 56.4V, not adjustable Flooded: 58V, not adjustable NMC/LiFePO4/Custom: 48V-60V
12 | 16651 | 410B |  | Read/Write | Float Charge Point | uint16_t | 0.1V | Lead-acid/Flooded: 54V, not adjustable NMC/LiFePO4: 50V-58V Custom: 48V-60V
13 | 16652 | 410C |  | Read/Write | Battery-to-Grid Switch Voltage Point | uint16_t | 0.1V | Lead-acid/Flooded: 44V-52V NMC/LiFePO4/Custom: 40V-50V
14 | 16653 | 410D |  | Read/Write | Return-to-Battery-Mode Voltage Point | uint16_t | 0.1V | Lead-acid/Flooded: 48V-58V NMC/LiFePO4/Custom: 46V-58V
15 | 16654 | 410E |  | Read/Write | Grid Low Voltage Point | uint16_t | 1V | APP : 90V-154V UPS : 170V-200V
16 | 16655 | 410F |  | Read/Write | Grid High Voltage Point | uint16_t | 1V | APP : 264V-280V UPS : 264V
17 | 16656 | 4110 |  | Read/Write | Parallel Mode | uint16_t | / | 0: Single-unit mode 1: Single-phase parallel mode 2: Three-phase parallel, Phase A 3: Three-phase parallel, Phase B 4: Three-phase parallel, Phase C
18 | 16657 | 4111 |  | Read/Write | Parallel Serial Number | uint16_t | / | 0-14
19 | 16658 | 4112 |  | Read/Write | Enable Equalization Mode Charging | uint16_t | / | 0:OFF 1:ON
20 | 16659 | 4113 |  | Read/Write | Equalization Voltage Point | uint16_t | 0.1V | 48V-60V
21 | 16660 | 4114 |  | Read/Write | Equalization Charge Time | uint16_t | 1min | 5-900, step 5
22 | 16661 | 4115 |  | Read/Write | Equalization Delay Time | uint16_t | 1min | 5-900, step 5
23 | 16662 | 4116 |  | Read/Write | Equalization Interval | uint16_t | day | 1-90
24 | 16663 | 4117 |  | Read/Write | Start Equalization Immediately | uint16_t | / | 0:OFF 1:ON
25 | 16664 | 4118 |  | Read/Write | Dual-Output Cutoff Voltage | uint16_t | 0.1V | 440-600：44V-60V
26 | 16665 | 4119 |  | Read/Write | Dual-Output Time | uint16_t | 1min | 5-900: 5min-900min 0xFFF1: Disable dual output 0xFFF2: Dual output unlimited time
27 | 16666 | 411A |  | Read/Write | Generator Enable | uint16_t | / | 0:OFF 1:ON
28 | 16667 | 411B |  | Read/Write | Generator Rated Power | uint16_t | 0.1KW | 0-65:0-6.5KW
29 | 16668 | 411C |  | Read/Write | Generator Max Power | uint16_t | 0.1KW | 0-65:0-6.5KW
30 | 16669 | 411D |  | Read/Write | Clear Generator Warning | uint16_t | / | 0:OFF 1:ON
31 | 16670 | 411E |  | Read/Write | BMS Protocol Selection | uint16_t | / | 0: Disable BMS function 1: CVTE protocol 2: Growatt protocol 3: Riyueyuan protocol 4: Pylontech protocol 5: Tietaproto (Tower) protocol 6: Peicheng protocol
32 | 16671 | 411F |  | Read/Write | BMS ID Selection | uint16_t | / | 0-15 0xFFF1: ID auto-search
33 | 16672 | 4120 |  | Read/Write | Low SOC Shutdown SOC Setting | uint16_t | 1% | 5-50 0xFFF1: Disable low SOC shutdown function
34 | 16673 | 4121 |  | Read/Write | Switch-to-Battery SOC Setting | uint16_t | 1% | 10-90 0xFFF1: Disable SOC switch-to-battery function
35 | 16674 | 4122 |  | Read/Write | Switch-to-Grid SOC Setting | uint16_t | 1% | 10-100 0xFFF1: Disable SOC switch-to-grid function
36 | 16675 | 4123 |  | Read/Write | Remote On/Off Enable | uint16_t | / | 0: Disable remote control 1: Enable remote control and power on 2: Enable remote control and power off
37 | 16676 | 4124 |  | Read/Write | Disable Charging | uint16_t | / | 0:OFF 1:ON
38 | 16677 | 4125 |  | Read/Write | Auto Backlight Off | uint16_t | / | 0:OFF 1:ON
39 | 16678 | 4126 |  | Read/Write | Reserved | / | / | /
40 | 16679 | 4127 |  | Read/Write | Restart on Over Temperature | uint16_t | / | 0:OFF 1:ON
41 | 16680 | 4128 |  | Read/Write | Restart on Overload | uint16_t | / | 0:OFF 1:ON
42 | 16681 | 4129 |  | Read/Write | Switch to Bypass on Overload | uint16_t | / | 0:OFF 1:ON
43 | 16682 | 412A |  | Read/Write | Low Power-Consumption Power Saving | uint16_t | / | 0:OFF 1:ON
44 | 16683 | 412B |  | Read/Write | Auto Grid Frequency Detection | uint16_t | / | 0:OFF 1:ON
45 | 16684 | 412C |  | Read/Write | Inverter Soft-Start After Output Relay Closes | uint16_t | / | 0:OFF 1:ON
46 | 16685 | 412D |  | Read/Write | Battery Open-Circuit Warning | uint16_t | / | 0:OFF 1:ON
47 | 16686 | 412E |  | Read/Write | Grid Feed-in Function Enable | uint16_t | / | 0: OFF 1: INT - internal sampling grid-tie 2: CT - external current transformer sampling grid-tie 3: MET - external meter communication grid-tie
48 | 16687 | 412F |  | Read/Write | Grid Feed-in Power | uint16_t | 0.1KW | 0-65:0-6.5KW
49 | 16688 | 4130 |  | Read/Write | Buzzer Mute | uint16_t | / | 0:OFF 1:ON
50 | 16689 | 4131 |  | Read/Write | Default Return to Main Screen Setting | uint16_t | / | 0:OFF 1:ON
51 | 16690 | 4132 |  | Read/Write | Main Input Change Warning | uint16_t | / | 0:OFF 1:ON
52 | 16691 | 4133 |  | Read/Write | Restore Default Settings | uint16_t | / | 0:OFF 1:ON
53 | 16692 | 4134 |  | Read/Write | Seconds Setting | uint16_t | 1sec | 0-59
54 | 16693 | 4135 |  | Read/Write | Minute | uint16_t | 1min | 0-59
55 | 16694 | 4136 |  | Read/Write | Hour | uint16_t | 1hour | 0-23
56 | 16695 | 4137 |  | Read/Write | Day | uint16_t | / | 0-31
57 | 16696 | 4138 |  | Read/Write | Month | uint16_t | / | 0-12
58 | 16697 | 4139 |  | Read/Write | Year | uint16_t | / | 0-99
59 | 16698 | 413A |  | Read/Write | Backup Power 1 | uint16_t | H | 0-23
60 | 16699 | 413B |  | Read/Write | Sell Power 1 | uint16_t | H | 0-23
61 | 16700 | 413C |  | Read/Write | Backup Power 2 | uint16_t | H | 0-23
62 | 16701 | 413D |  | Read/Write | Sell Power 2 | uint16_t | H | 0-23
63 | 16702 | 413E |  | Read/Write | Power On | uint16_t | H | 0-23
64 | 16703 | 413F |  | Read/Write | Power Off | uint16_t | H | 0-23
65 | 16704 | 4140 |  | Read/Write | Model Configuration | uint16_t |  | 0: Auto-detect (takes effect after next power-on) 1: Low-spec model 2: Mid-spec model 3: High-spec model
66 | 16705 | 4141 |  | Read/Write | Screen Type | uint16_t |  | 0：TRB8131 1：B00346 2: CNKD0601/CNKD0602
67 | 16706 | 4142 |  | Read/Write | Max Discharge Current | uint16_t | A | 0-30: 10-160A (step 5A) 0xFFF1: OFF [Applies to VMH5KU/VMH6KU, VML1K2; VMH5KU supports up to 160A, VMH6KU up to 140A, VML1K2 up to 120A]
68 | #ERROR! | 4143 |  | Read/Write | Wifi Connection Status | uint16_t |  | For use by the Wifi module 1: Wifi not connected to access point 2: Wifi connecting to access point 3: Wifi connected to access point 4: Wifi connected to cloud server 0xFF: Disable this flag
69 | #ERROR! | 4144 |  | Read/Write | Auto Grid Feed-in Power Switch Time 1 | uint16_t | H | 0-23
70 | #ERROR! | 4145 |  | Read/Write | Auto Grid Feed-in Power Switch Time 2 | uint16_t | H | 0-23
71 | #ERROR! | 4146 |  | Read/Write | Auto Grid Feed-in Power Switch 1 | uint16_t | 0.1KW | 0-65:0-6.5KW
72 | #ERROR! | 4147 |  | Read/Write | Auto Grid Feed-in Power Switch 2 | uint16_t | 0.1KW | 0-65:0-6.5KW
73 | 16712 | 4148 |  | Read/Write | Set Fan Speed to 100 Before Shutdown Flag | uint16_t |  | 0: Normal operation 1: Set fan speed to 100 before shutdown, to address low-power fans that fail to stop when the board powers off [Applies only to VML1K2]
74 | 16713 | 4149 |  | Read/Write | Set Inverter Current Reference Value When Output Power Is Below 50W | uint16_t | 0.01A | Default value is 26, setting range is 0-200 [Applies to VMH5KU/VMH6KU]
75 | 16714 | 414A |  | Read/Write | Set Button Reverse | uint16_t |  | 0: Down button increases page value 1: Down button decreases page value [Applies to VMH5KU/VMH6KU]
76 | 16715 | 414B |  | Read/Write | Set Dual-Output Cutoff SOC | uint16_t |  | 5-90: Dual-output cutoff SOC 0xFFF1: Disable this function [Applies to VMH5KU/VMH6KU]
76 | 16715 | 414C |  | Read/Write | Prevent Power-Off | uint16_t |  | 0: Inactive 1: Prevent power-off Once set, the unit will not enter shutdown mode even if it is otherwise eligible to power off. The prevent-power-off flag resets 1 minute after each write; the counter resets on each write.